## List of Room
PERHITUNGAN KEBUTUHAN AIR HANDLING UNIT (AHU) PADA AKOMODASI KAPAL
Halaman :
LIST RUANGAN AKOMODASI & DIMENSI
NO. | DECK | ROOM | P (m) | L (m) | T (m) | A (m2) | V (m3)
Main Deck
1 |  | Mess Room | 4.64 | 3.98 | 2.5 | 18.4672 | 46.168
2 |  | Quarter Master & Steward Room | 3 | 4.1 | 2.5 | 12.3 | 30.75
3 |  | Boatswain & Seaman Room | 3 | 4.24 | 2.5 | 12.72 | 31.8
4 |  | Oiler (2p) Room | 3 | 4.1 | 2.5 | 12.3 | 30.75
5 |  | Pumpman (2p) Room | 3 | 4.2 | 2.5 | 12.6 | 31.5
6 |  | Fireman (2p) Room | 3 | 4.24 | 2.5 | 12.72 | 31.8
7 |  | Boys (2p) Room | 3 | 4.2 | 2.5 | 12.6 | 31.5
Poop Deck
1 |  | Chief Cook Room | 3 | 3.4 | 2.4 | 10.2 | 24.48
2 |  | Second Engineer Room | 3 | 3.4 | 2.4 | 10.2 | 24.48
3 |  | Musholla | 3 | 3.4 | 2.4 | 10.2 | 24.48
4 |  | Electrician Room | 3 | 3.4 | 2.4 | 10.2 | 24.48
5 |  | Smoking Room | 3.5 | 4 | 2.4 | 14 | 33.6
6 |  | Mess Room | 3.5 | 3.4 | 2.4 | 11.9 | 28.56
Boat Deck
1 |  | Chief Officer % Engineer Office | 3.55 | 5 | 2.4 | 17.75 | 42.6
2 |  | Chief Officer Room | 4.4 | 3.41 | 2.4 | 15.004 | 36.0096
3 |  | Chief Engineer Room | 4.4 | 3.41 | 2.4 | 15.004 | 36.0096
4 |  | Second Officer Room | 4 | 3.41 | 2.4 | 13.64 | 32.736
5 |  | Medical Room | 4 | 3.41 | 2.4 | 13.64 | 32.736
Bridge Deck
1 |  | Master Room | 6.6 | 3.23 | 2.4 | 21.318 | 51.1632
2 |  | Master Office | 3.55 | 2.98 | 2.4 | 10.579 | 25.3896
3 |  | Meeting Room | 3.55 | 3.2 | 2.4 | 11.36 | 27.264
4 |  | Radio Operator Room | 4.35 | 3.41 | 2.4 | 14.8335 | 35.6004
5 |  | Library | 2.25 | 3.41 | 2.4 | 7.6725 | 18.414
Navigation Deck
1 |  | Navigation Room | 6.925 | 3.717 | 2.5 | 25.7402 | 64.3506
2 |  | Radio Room | 6.925 | 3.717 | 2.5 | 25.7402 | 64.3506

## Summary
PERHITUNGAN KEBUTUHAN AIR HANDLING UNIT (AHU) PADA AKOMODASI KAPAL
Halaman :
COOLING SUMMARY
SPACE | DECK | SIDE | FRAMES | Volume (ft3) | Heat Area (ft2) | BTU/HR |  |  | SHF | OUTSIDE AIR BASED ON * |  |  | CFM | R/C TOTAL AIR | Air Quantity (l/s) | Friction Loss (Pa/mm) | Duct Diameter (mm) | Rect. Duct Size (mm) | Uk. Diffuser | l/s | Jumlah Diffuser
|  | SIDE | FRAMES |  |  | SENS. | LATENT | TOTAL |  | R/C | PERS. | EXH. | [5 empty] | L x W
Pantry | Poop Deck | P | 06 to 11 | 867.0465 | 664.2316 | 4077.055 | 790 | 4867.055 | 0.83768 | 28.9016 | 15 | 15 | 152 | 28.9016 | 71.744
Mess Room |  | P | 11 to 16 | 1008.5878 | 769.3885 | 5347.1072 | 4000 | 9347.1072 | 0.57206 | 33.6196 | 120 | 120 | 199 | 120 | 93.928
Chief Cook Room |  | P | 20 to 24 | 867.0465 | 662.8797 | 2171.0295 | 500 | 2671.0295 | 0.81281 | 28.9016 | 15 | 15 | 81 | 28.9016 | 38.232
Musholla |  | S | 11 to 16 | 867.0465 | 732.7589 | 2473.1104 | 1000 | 3473.1104 | 0.71207 | 28.9016 | 30 | 30 | 92 | 30 | 43.424
Electrician Room |  | S | 16 to 20 | 867.0465 | 728.1089 | 1399.0661 | 500 | 1899.0661 | 0.73671 | 28.9016 | 15 | 15 | 52 | 28.9016 | 24.544
Second Engineer Room |  | S | 20 to 25 | 867.0465 | 693.686 | 2154.4182 | 500 | 2654.4182 | 0.81163 | 28.9016 | 15 | 15 | 80 | 28.9016 | 37.76
Smoking Room |  | C | 20 to 25 | 1186.5739 | 879.9617 | 4612.8964 | 2000 | 6612.8964 | 0.69756 | 39.5525 | 60 | 60 | 171 | 60 | 80.712
[6 empty] | 22234.6828 | 9290 | 31524.6828 |  |  |  |  | 827

## Pantry
H | U | D |  |  |  | 1 m = | 3.28 | ft
SPACE |  | SPACE NO. |  | MAIN DECK |  | FRAMES | SPACE TEMP COOLING |  |  |  | 78.8 | °F | SPACE TEMP HEATING |  | 70 | °F
Pantry |  | MD/SB/4 |  |  |  | 06 to 11 | [10 empty] | Kondisi Temperature udara yang didesain. | 26°C | 78,8°F
ADJOINING SPACE | LOAD | INSUL | U | DIMENSION (m2) |  | AREA (Ft ²) | TO | TD | U | QS | QL | QT | TO | TD | U | Qw
| KEY | TYPE | KEY | Panjang | Tinggi/Lebar
Depan = MessRoom | 4 | 10 | H | 3.41 | 2.4 | 88.0918 | TO: 78.8; TD: 0; U: 0.361; QS: 0; QT: 0
Belakang = Outside/Solar | 5 | 54 | H | 3.41 | 2.4 | 88.0918 | TO: 125; TD: 46.2; U: 0.212; QS: 862.8059; QT: 862.8059 |  |  |  | Glass Solar Factor | saya pakai | 95F |  | Equipment
Kanan = Gangway | 6 | 54 | H | 3 | 2.4 | 77.5001 | TO: 80; TD: 1.2; U: 0.191; QS: 17.763; QT: 17.763
Kiri = Outdoor /Portside Weather | 3 | 54 | H | 3 | 2.4 | 77.5001 | TO: 95; TD: 16.2; U: 0.196; QS: 246.0783; QT: 246.0783
Solar (window) | 3 |  | GLASS |  | 0.4 | 2.7039 | QS: 432.6209; QT: 432.6209
atas = Outdoor/ Weather | 1 | 54 | D | 3 | 3.41 | 110.1147 | TO: 95; TD: 16.2; U: 0.176; QS: 313.959; QT: 313.959
bawah = Messroom | 2 | 10 | U | 3 | 3.41 | 110.1147 | TO: 78.8; TD: 0; U: 0.435; QS: 0; QT: 0 | [8 empty] | ql = q ,dl ×U F
lampu | 7 |  |  | 3 | 3.41 | 110.1147 | QS: 770.8029; QT: 770.8029
qs = q ,ds ×U F × H F
Equipment : | 8 | [17 empty] | Udara Luar
Dishwasher | 8 | [5 empty] | QS: 280; QL: 290; QT: 570
Electric Stove (250 Watt) | 8 | [5 empty] | QS: 853.025; QT: 853.025 | [8 empty] | Jika tudung buang dipasang di atas peralatan, gunakan Faktor Tudung, H.F., 0,5. Beban laten untuk peralatan tersebut dianggap nol. Gunakan H.F. = 1,0 dalam Persamaan 3-6 ketika tudung buang tidak dipasang di atas peralatan. Lihat Tabel 3-6 untuk Faktor Penggunaan yang direkomendasikan, U.F
Personel
manusia (latent & sensibel) | 9 | [5 empty] | QS: 300; QL: 500; QT: 800 | Pemilihan Insulation
TOTAL HEAT | [6 empty] | QS: 4077.055; QL: 790; QT: 4867.055 |  |  |  | Lighting Loads
q=A x LC
Occupancy
ΔT = | 25 | °F | Vol. = |  | 867.0465 | Ft³ | TO: Out. Air =; TD: 15; U: cfm; QL: `
NOTES : GLASS SOLAR LOAD = 160 BTU/HR/ft² x 8,79 ft² = BTU/HR
SHF (Sensible Heat factor)= | Qs/Qt = | 0.83768 |  |  | Q = | Qs/1.08 x ΔT | TO: 151.002; TD: use; U: 152; QS: Cfm
Min. Out. Air (1) Occupancy = | 1 | 15 | 15 | (2) R/C = | 28.9016 |  | TO: (3) Exhaust throuht Rad. Equip. =; QL: -; TO: HULL or JOB Numnber :
Check by : GEK/MAM
KEY |  | SYMBOLS |  |  |  |  | TO: SUMMARY; TO: Calculated by : Vieri Pramudya Dirgantara
1 = Deck Over |  | Qs = Heat Load, BTU/Hr, Sensible |  |  |  |  | TO: Sq. Ft.; TD: 664.2316; QS: ƩQL; QL: 790; TO: HEATING & COOLING LOAD CALCULATIONS |  |  |  | Heat Gain Personal
2 = Deck Under |  | QL = Heat Load, BTU/Hr, Latent |  |  |  |  | TO: Height; TD: 2.4; QS: ƩQT; QL: 4867.055 | [10 empty] | Hunian Udara luar ruangan minimum berdasarkan hunian kamar adalah 12 CFM / orang untuk ruang hunian tinggi (misalnya, ruang rekreasi, ruang makan dan kamar mess) dan 15 CFM / orang untuk ruang ber-AC dengan hunian rendah (misalnya, kabin dan kantor). Tarif ini hanya akan ditingkatkan untuk mencapai keseimbangan udara dalam setiap subdivisi, tetapi tidak boleh melebihi 50 CFM / orang.
3 = Outboard Bhd or Shell |  | QT = Heat Load, BTU/Hr, Total |  |  |  |  | TO: Volume; TD: 867.0465; QS: Q; QL: 152
4 = Forward Bulkhead |  | QW = Heat Load, BTU/Hr, Winter |  |  |  |  | TO: R or C; TD: 28.9016
5 = After Bulkhead |  | U = Transmittance, BTU/Sq. Ft. Hr. °F |  |  |  |  | TO: ƩQs; TD: 4077.055
6 = Inboard Bulkhead |  | TD = Temperature Differences |  |  |  |  | TO: SHF; TD: 0.83768; TO: REV; U: SHEET NO OF
7 = Lights |  | TO = Temp of Adjoining Space or Outside
8 = Equipment
9= Personnel
Kode | [6 empty] | U: Uk.Jendela; QL: 400; QT: mm; TO: 0.4; TD: m
10 | Tidak mengalami perpindahan panas | [5 empty] | U: Jumalah Jendela; QL: 2 | [10 empty] | Infiltrasi Untuk ruang seperti Ruang Kemudi (Rumah Percontohan) dengan pintu yang terbuka langsung ke cuaca, laju perubahan udara luar ruangan minimum adalah 60 menit, tetapi tidak boleh melebihi 50 CFM / orang.
54 | Mengalami perpindahan panas | [5 empty] | TO: Volume Ruangan
[7 empty] | p | 3
[7 empty] | l | 3.41
[7 empty] | t | 2.4 | [5 empty] | H | U | D
[8 empty] | 24.552 | m3
[8 empty] | 867.0465 | ft3
[6 empty] | 1 Watt= | TO: 3.4121; TD: BTU/hr
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Yang menghadap depan kapal
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Yang menghadap belakang kapal
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Depan kamar (pintu masuk)
Note on C9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Menghadap luar lambung kapal
Note on C11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian atas
Note on C12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian bawah
Note on C13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian bawah
Note on C15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: peralatan
Note on D6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo tidak bersebelahan dengan sumber panas kasih insulasi key 5,6, 10
Note on D7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo tidak bersebelahan dengan sumber panas kasih insulasi key 5,6, 10
Note on D9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on I8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on I12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on I14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on L10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A X Gsf Nilai Gsf didapat dari tabel 3-3 single boundaries
Note on L13: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L15: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jumlah orang x beban latent Beban sensibel di tabel 3-8 all other sesuai suhu dalam ruangan
Note on M20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jumlah orang x beban latent Beban laten di tabel 3-8 all other sesuai suhu dalam ruangan

## Mess Room
H | U | D |  |  |  | 1 m = | 3.28 | ft
SPACE |  | SPACE NO. |  | MAIN DECK |  | FRAMES | SPACE TEMP COOLING |  |  |  | 78.8 | °F | SPACE TEMP HEATING |  | 70 | °F
Mess Room |  | MD/SB/4 |  |  |  | 11 to 16 | [10 empty] | Kondisi Temperature udara yang didesain. | 26°C | 78,8°F
ADJOINING SPACE | LOAD | INSUL | U | DIMENSION (m2) |  | AREA (Ft ²) | TO | TD | U | QS | QL | QT | TO | TD | U | Qw
| KEY | TYPE | KEY | Panjang | Tinggi/Lebar
Depan = Locker Room | 4 | 54 | H | 3.41 | 2.4 | 88.0918 | TO: 110; TD: 31.2; U: 0.191; QS: 524.9564; QT: 524.9564
Belakang = Pamtry | 5 | 10 | H | 3.41 | 2.4 | 88.0918 | TO: 78.8; TD: 0; U: 0.328; QS: 0; QT: 0 |  |  |  | Glass Solar Factor | saya pakai | 95F |  | Equipment
Kanan = Gangway | 6 | 54 | H | 3.5 | 2.4 | 90.4168 | TO: 80; TD: 1.2; U: 0.191; QS: 20.7235; QT: 20.7235
Kiri = Outdoor/Portside Weather | 3 | 54 | H | 3.5 | 2.4 | 90.4168 | TO: 95; TD: 16.2; U: 0.196; QS: 287.0913; QT: 287.0913
Solar (window) | 3 |  | GLASS |  | 0.4 | 1.3519 | QS: 216.3105; QT: 216.3105
atas = Second Officer Room | 1 | 10 | D | 2.9 | 3.41 | 106.4442 | TO: 78.8; TD: 0; U: 0.272; QS: 0; QT: 0
atas = Outdoor/Weather | 1 | 54 | D | 0.6 | 3.41 | 22.0229 | TO: 95; TD: 16.2; U: 0.176; QS: 62.7918; QT: 62.7918 | [8 empty] | ql = q ,dl ×U F
bawah = Quarter Master & Steward Room | 2 | 10 | U | 3 | 4.1 | 132.396 | TO: 78.8; TD: 0; U: 0.435; QS: 0; QT: 0
bawah = Boys (2p) | 2 | 10 | U | 0.5 | 4.1 | 22.066 | TO: 78.8; TD: 0; U: 0.435; QS: 0; QT: 0
lampu | 7 |  |  | 3.5 | 3.4 | 128.0904 | QS: 1152.8137; QT: 1152.8137 | [8 empty] | qs = q ,ds ×U F × H F
Udara Luar
Equipment : | 8
TV (200 Watt) | 8 | [5 empty] | QS: 682.42; QT: 682.42 | [8 empty] | Jika tudung buang dipasang di atas peralatan, gunakan Faktor Tudung, H.F., 0,5. Beban laten untuk peralatan tersebut dianggap nol. Gunakan H.F. = 1,0 dalam Persamaan 3-6 ketika tudung buang tidak dipasang di atas peralatan. Lihat Tabel 3-6 untuk Faktor Penggunaan yang direkomendasikan, U.F
Personel
manusia (latent & sensibel) | 9 | [5 empty] | QS: 2400; QL: 4000; QT: 6400 | Pemilihan Insulation
TOTAL HEAT | [6 empty] | QS: 5347.1072; QL: 4000; QT: 9347.1072 |  |  |  | Lighting Loads
q=A x LC
Occupancy
ΔT = | 25 | °F | Vol. = |  | 1008.5878 | Ft³ | TO: Out. Air =; TD: 120; U: cfm; QL: `
NOTES : GLASS SOLAR LOAD = 160 BTU/HR/ft² x 8,79 ft² = BTU/HR
SHF (Sensible Heat factor)= | Qs/Qt = | 0.57206 |  |  | Q = | Qs/1.08 x ΔT | TO: 198.041; TD: use; U: 199; QS: Cfm
Min. Out. Air (1) Occupancy = | 8 | 15 | 120 | (2) R/C = | 33.6196 |  | TO: (3) Exhaust throuht Rad. Equip. =; QL: -; TO: HULL or JOB Numnber :
Check by : GEK/MAM
KEY |  | SYMBOLS |  |  |  |  | TO: SUMMARY; TO: Calculated by : Vieri Pramudya Dirgantara
1 = Deck Over |  | Qs = Heat Load, BTU/Hr, Sensible |  |  |  |  | TO: Sq. Ft.; TD: 769.3885; QS: ƩQL; QL: 4000; TO: HEATING & COOLING LOAD CALCULATIONS |  |  |  | Heat Gain Personal
2 = Deck Under |  | QL = Heat Load, BTU/Hr, Latent |  |  |  |  | TO: Height; TD: 2.4; QS: ƩQT; QL: 9347.1072 | [10 empty] | Hunian Udara luar ruangan minimum berdasarkan hunian kamar adalah 12 CFM / orang untuk ruang hunian tinggi (misalnya, ruang rekreasi, ruang makan dan kamar mess) dan 15 CFM / orang untuk ruang ber-AC dengan hunian rendah (misalnya, kabin dan kantor). Tarif ini hanya akan ditingkatkan untuk mencapai keseimbangan udara dalam setiap subdivisi, tetapi tidak boleh melebihi 50 CFM / orang.
3 = Outboard Bhd or Shell |  | QT = Heat Load, BTU/Hr, Total |  |  |  |  | TO: Volume; TD: 1008.5878; QS: Q; QL: 199
4 = Forward Bulkhead |  | QW = Heat Load, BTU/Hr, Winter |  |  |  |  | TO: R or C; TD: 33.6196
5 = After Bulkhead |  | U = Transmittance, BTU/Sq. Ft. Hr. °F |  |  |  |  | TO: ƩQs; TD: 5347.1072
6 = Inboard Bulkhead |  | TD = Temperature Differences |  |  |  |  | TO: SHF; TD: 0.57206; TO: REV; U: SHEET NO OF
7 = Lights |  | TO = Temp of Adjoining Space or Outside
8 = Equipment
9= Personnel
Kode | [6 empty] | U: Uk.Jendela; QL: 400; QT: mm; TO: 0.4; TD: m
10 | Tidak mengalami perpindahan panas | [5 empty] | U: Jumlah Jendela; QL: 3 | [10 empty] | Infiltrasi Untuk ruang seperti Ruang Kemudi (Rumah Percontohan) dengan pintu yang terbuka langsung ke cuaca, laju perubahan udara luar ruangan minimum adalah 60 menit, tetapi tidak boleh melebihi 50 CFM / orang.
54 | Mengalami perpindahan panas | [5 empty] | TO: Volume Ruangan
[7 empty] | p | 3.5
[7 empty] | l | 3.4
[7 empty] | t | 2.4 | [5 empty] | H | U | D
[8 empty] | 28.56 | m3
[8 empty] | 1008.5878 | ft3
[6 empty] | 1 Watt= | TO: 3.4121; TD: BTU/hr
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Yang menghadap depan kapal
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Yang menghadap belakang kapal
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Depan kamar (pintu masuk)
Note on C9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Menghadap luar lambung kapal
Note on C11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian atas
Note on C12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian atas
Note on C13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian bawah
Note on C14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian bawah
Note on C15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: peralatan
Note on D6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo tidak bersebelahan dengan sumber panas kasih insulasi key 5,6, 10
Note on D7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo tidak bersebelahan dengan sumber panas kasih insulasi key 5,6, 10
Note on D9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on I8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on I11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: karena permukaan horizontal terpapar suhu lingkungan maka suhu yang dipake 145 sesuai tabel 3-3
Note on I12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: karena permukaan horizontal terpapar suhu lingkungan maka suhu yang dipake 145 sesuai tabel 3-3
Note on I13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on I14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on L10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A X Gsf Nilai Gsf didapat dari tabel 3-3 single boundaries
Note on L15: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L16: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jumlah orang x beban latent Beban sensibel di tabel 3-8 all other sesuai suhu dalam ruangan
Note on M20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jumlah orang x beban latent Beban laten di tabel 3-8 all other sesuai suhu dalam ruangan

## Chief Cook Room
H | U | D |  |  |  | 1 m = | 3.28 | ft
SPACE |  | SPACE NO. |  | MAIN DECK |  | FRAMES | SPACE TEMP COOLING |  |  |  | 78.8 | °F | SPACE TEMP HEATING |  | 70 | °F
Chief Cook Room |  | MD/SB/4 |  |  |  | 20 to 24 | [10 empty] | Kondisi Temperature udara yang didesain. | 26°C | 78,8°F
ADJOINING SPACE | LOAD | INSUL | U | DIMENSION (m2) |  | AREA (Ft ²) | TO | TD | U | QS | QL | QT | TO | TD | U | Qw
| KEY | TYPE | KEY | Panjang | Tinggi/Lebar
Depan = Outdoor/Solar | 4 | 54 | H | 3.41 | 2.4 | 88.0918 | TO: 125; TD: 46.2; U: 0.212; QS: 862.8059; QT: 862.8059
Belakang = Gangway | 5 | 54 | H | 3.41 | 2.4 | 88.0918 | TO: 80; TD: 1.2; U: 0.191; QS: 20.1906; QT: 20.1906 |  |  |  | Glass Solar Factor | saya pakai | 95F |  | Equipment
Kanan = Gangway | 6 | 54 | H | 3 | 2.4 | 77.5001 | TO: 80; TD: 1.2; U: 0.191; QS: 17.763; QT: 17.763
Kiri = Outdoor/Portside Weather | 3 | 54 | H | 3 | 2.4 | 77.5001 | TO: 95; TD: 16.2; U: 0.196; QS: 246.0783; QT: 246.0783
Solar (window) | 3 |  | GLASS |  | 0.4 | 1.3519 | QS: 216.3105; QT: 216.3105
atas =Chief Engineer Room | 1 | 10 | D | 3 | 3.41 | 94.6147 | TO: 78.8; TD: 0; U: 0.272; QS: 0; QT: 0
atas =Toilet Chief Engineer Room | 1 | 54 | D | 1.2 | 1.2 | 15.5 | TO: 85; TD: 6.2; U: 0.169; QS: 16.2409; QT: 16.2409 | [8 empty] | ql = q ,dl ×U F
bawah = Boatswain & Seaman Room | 2 | 10 | U | 3 | 3.41 | 110.1147 | TO: 78.8; TD: 0; U: 0.435; QS: 0; QT: 0
lampu | 7 |  |  | 3 | 3.41 | 110.1147 | QS: 440.4588; QT: 440.4588
qs = q ,ds ×U F × H F
Udara Luar
Equipment : | 8
Handphone (15 Watt) | 8 | [5 empty] | QS: 51.1815 | [8 empty] | Jika tudung buang dipasang di atas peralatan, gunakan Faktor Tudung, H.F., 0,5. Beban laten untuk peralatan tersebut dianggap nol. Gunakan H.F. = 1,0 dalam Persamaan 3-6 ketika tudung buang tidak dipasang di atas peralatan. Lihat Tabel 3-6 untuk Faktor Penggunaan yang direkomendasikan, U.F
Personel
manusia (latent & sensibel) | 9 | [5 empty] | QS: 300; QL: 500; QT: 800 | Pemilihan Insulation
TOTAL HEAT | [6 empty] | QS: 2171.0295; QL: 500; QT: 2671.0295 |  |  |  | Lighting Loads
q=A x LC
Occupancy
ΔT = | 25 | °F | Vol. = |  | 867.0465 | Ft³ | TO: Out. Air =; TD: 15; U: cfm; QL: `
NOTES : GLASS SOLAR LOAD = 160 BTU/HR/ft² x 8,79 ft² = BTU/HR
SHF (Sensible Heat factor)= | Qs/Qt = | 0.81281 |  |  | Q = | Qs/1.08 x ΔT | TO: 80.4085; TD: use; U: 81; QS: Cfm
Min. Out. Air (1) Occupancy = | 1 | 15 | 15 | (2) R/C = | 28.9016 |  | TO: (3) Exhaust throuht Rad. Equip. =; QL: -; TO: HULL or JOB Numnber :
Check by : GEK/MAM
KEY |  | SYMBOLS |  |  |  |  | TO: SUMMARY; TO: Calculated by : Vieri Pramudya Dirgantara
1 = Deck Over |  | Qs = Heat Load, BTU/Hr, Sensible |  |  |  |  | TO: Sq. Ft.; TD: 662.8797; QS: ƩQL; QL: 500; TO: HEATING & COOLING LOAD CALCULATIONS |  |  |  | Heat Gain Personal
2 = Deck Under |  | QL = Heat Load, BTU/Hr, Latent |  |  |  |  | TO: Height; TD: 2.4; QS: ƩQT; QL: 2671.0295 | [10 empty] | Hunian Udara luar ruangan minimum berdasarkan hunian kamar adalah 12 CFM / orang untuk ruang hunian tinggi (misalnya, ruang rekreasi, ruang makan dan kamar mess) dan 15 CFM / orang untuk ruang ber-AC dengan hunian rendah (misalnya, kabin dan kantor). Tarif ini hanya akan ditingkatkan untuk mencapai keseimbangan udara dalam setiap subdivisi, tetapi tidak boleh melebihi 50 CFM / orang.
3 = Outboard Bhd or Shell |  | QT = Heat Load, BTU/Hr, Total |  |  |  |  | TO: Volume; TD: 867.0465; QS: Q; QL: 81
4 = Forward Bulkhead |  | QW = Heat Load, BTU/Hr, Winter |  |  |  |  | TO: R or C; TD: 28.9016
5 = After Bulkhead |  | U = Transmittance, BTU/Sq. Ft. Hr. °F |  |  |  |  | TO: ƩQs; TD: 2171.0295
6 = Inboard Bulkhead |  | TD = Temperature Differences |  |  |  |  | TO: SHF; TD: 0.81281; TO: REV; U: SHEET NO OF
7 = Lights |  | TO = Temp of Adjoining Space or Outside
8 = Equipment
9= Personnel
Kode | [6 empty] | U: Uk.Jendela; QL: 400; QT: mm; TO: 0.4; TD: m
10 | Tidak mengalami perpindahan panas | [25 empty] | Infiltrasi Untuk ruang seperti Ruang Kemudi (Rumah Percontohan) dengan pintu yang terbuka langsung ke cuaca, laju perubahan udara luar ruangan minimum adalah 60 menit, tetapi tidak boleh melebihi 50 CFM / orang.
54 | Mengalami perpindahan panas | [5 empty] | TO: Volume Ruangan
[7 empty] | p | 3
[7 empty] | l | 3.41
[7 empty] | t | 2.4 | [5 empty] | H | U | D
[8 empty] | 24.552 | m3
[8 empty] | 867.0465 | ft3
[6 empty] | 1 Watt= | TO: 3.4121; TD: BTU/hr
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Yang menghadap depan kapal
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Yang menghadap belakang kapal
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Depan kamar (pintu masuk)
Note on C9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Menghadap luar lambung kapal
Note on C11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian atas
Note on C12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian atas
Note on C13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian bawah
Note on C14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: peralatan
Note on D7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo tidak bersebelahan dengan sumber panas kasih insulasi key 5,6, 10
Note on D9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on I8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on I13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on L10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A X Gsf Nilai Gsf didapat dari tabel 3-3 single boundaries
Note on L14: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L15: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L16: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jumlah orang x beban latent Beban sensibel di tabel 3-8 all other sesuai suhu dalam ruangan
Note on M20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jumlah orang x beban latent Beban laten di tabel 3-8 all other sesuai suhu dalam ruangan

## Musholla
H | U | D |  |  |  | 1 m = | 3.28 | ft
SPACE |  | SPACE NO. |  | MAIN DECK |  | FRAMES | SPACE TEMP COOLING |  |  |  | 78.8 | °F | SPACE TEMP HEATING |  | 70 | °F
Musholla |  | MD/SB/4 |  |  |  | 11 to 16 | [10 empty] | Kondisi Temperature udara yang didesain. | 26°C | 78,8°F
ADJOINING SPACE | LOAD | INSUL | U | DIMENSION (m2) |  | AREA (Ft ²) | TO | TD | U | QS | QL | QT | TO | TD | U | Qw
| KEY | TYPE | KEY | Panjang | Tinggi/Lebar
Depan = Electrician Room | 4 | 10 | H | 3.4 | 2.4 | 87.8334 | TO: 78.8; TD: 0; U: 0.361; QS: 0; QT: 0
Belakang = Toilet | 5 | 54 | H | 3.4 | 2.4 | 87.8334 | TO: 105; TD: 26.2; U: 0.191; QS: 439.536; QT: 439.536 |  |  |  | Glass Solar Factor | saya pakai | 95F |  | Equipment
Kanan = Outdoor/Starboard Weather | 6 | 54 | H | 3.49 | 3 | 112.698 | TO: 95; TD: 16.2; U: 0.196; QS: 357.8388; QT: 357.8388
Kiri = Gangway | 3 | 54 | H | 3.49 | 3 | 112.698 | TO: 80; TD: 1.2; U: 0.191; QS: 25.8304; QT: 25.8304
Solar (window) | 3 |  | GLASS |  | 0.4 | 1.3519 | QS: 216.3105; QT: 216.3105
atas = Medical Room | 1 | 10 | D | 2.4 | 3.41 | 88.0918 | TO: 78.8; TD: 0; U: 0.272; QS: 0; QT: 0
atas = Outdoor/Weather | 1 | 54 | D | 0.6 | 3.41 | 22.0229 | TO: 95; TD: 16.2; U: 0.176; QS: 62.7918; QT: 62.7918 | [8 empty] | ql = q ,dl ×U F
bawah = Oiler (2p)Room | 2 | 10 | U | 3 | 3.41 | 110.1147 | TO: 78.8; TD: 0; U: 0.435; QS: 0; QT: 0
lampu | 7 |  |  | 3 | 3.41 | 110.1147 | QS: 770.8029; QT: 770.8029
qs = q ,ds ×U F × H F
Udara Luar
Equipment : | 8
Jika tudung buang dipasang di atas peralatan, gunakan Faktor Tudung, H.F., 0,5. Beban laten untuk peralatan tersebut dianggap nol. Gunakan H.F. = 1,0 dalam Persamaan 3-6 ketika tudung buang tidak dipasang di atas peralatan. Lihat Tabel 3-6 untuk Faktor Penggunaan yang direkomendasikan, U.F
Personel
manusia (latent & sensibel) | 9 | [5 empty] | QS: 600; QL: 1000; QT: 1600 | Pemilihan Insulation
TOTAL HEAT | [6 empty] | QS: 2473.1104; QL: 1000; QT: 3473.1104 |  |  |  | Lighting Loads
q=A x LC
Occupancy
ΔT = | 25 | °F | Vol. = |  | 867.0465 | Ft³ | TO: Out. Air =; TD: 30; U: cfm; QL: `
NOTES : GLASS SOLAR LOAD = 160 BTU/HR/ft² x 8,79 ft² = BTU/HR
SHF (Sensible Heat factor)= | Qs/Qt = | 0.71207 |  |  | Q = | Qs/1.08 x ΔT | TO: 91.5967; TD: use; U: 92; QS: Cfm
Min. Out. Air (1) Occupancy = | 2 | 15 | 30 | (2) R/C = | 28.9016 |  | TO: (3) Exhaust throuht Rad. Equip. =; QL: -; TO: HULL or JOB Numnber :
Check by : GEK/MAM
KEY |  | SYMBOLS |  |  |  |  | TO: SUMMARY; TO: Calculated by : Vieri Pramudya Dirgantara
1 = Deck Over |  | Qs = Heat Load, BTU/Hr, Sensible |  |  |  |  | TO: Sq. Ft.; TD: 732.7589; QS: ƩQL; QL: 1000; TO: HEATING & COOLING LOAD CALCULATIONS |  |  |  | Heat Gain Personal
2 = Deck Under |  | QL = Heat Load, BTU/Hr, Latent |  |  |  |  | TO: Height; TD: 2.4; QS: ƩQT; QL: 3473.1104 | [10 empty] | Hunian Udara luar ruangan minimum berdasarkan hunian kamar adalah 12 CFM / orang untuk ruang hunian tinggi (misalnya, ruang rekreasi, ruang makan dan kamar mess) dan 15 CFM / orang untuk ruang ber-AC dengan hunian rendah (misalnya, kabin dan kantor). Tarif ini hanya akan ditingkatkan untuk mencapai keseimbangan udara dalam setiap subdivisi, tetapi tidak boleh melebihi 50 CFM / orang.
3 = Outboard Bhd or Shell |  | QT = Heat Load, BTU/Hr, Total |  |  |  |  | TO: Volume; TD: 867.0465; QS: Q; QL: 92
4 = Forward Bulkhead |  | QW = Heat Load, BTU/Hr, Winter |  |  |  |  | TO: R or C; TD: 28.9016
5 = After Bulkhead |  | U = Transmittance, BTU/Sq. Ft. Hr. °F |  |  |  |  | TO: ƩQs; TD: 2473.1104
6 = Inboard Bulkhead |  | TD = Temperature Differences |  |  |  |  | TO: SHF; TD: 0.71207; TO: REV; U: SHEET NO OF
7 = Lights |  | TO = Temp of Adjoining Space or Outside
8 = Equipment
9= Personnel
Kode | [6 empty] | U: Uk.Jendela; QL: 400; QT: mm; TO: 0.4; TD: m
10 | Tidak mengalami perpindahan panas | [25 empty] | Infiltrasi Untuk ruang seperti Ruang Kemudi (Rumah Percontohan) dengan pintu yang terbuka langsung ke cuaca, laju perubahan udara luar ruangan minimum adalah 60 menit, tetapi tidak boleh melebihi 50 CFM / orang.
54 | Mengalami perpindahan panas | [5 empty] | TO: Volume Ruangan
[7 empty] | p | 3
[7 empty] | l | 3.41
[7 empty] | t | 2.4 | [5 empty] | H | U | D
[8 empty] | 24.552 | m3
[8 empty] | 867.0465 | ft3
[6 empty] | 1 Watt= | TO: 3.4121; TD: BTU/hr
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Yang menghadap depan kapal
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Yang menghadap belakang kapal
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Depan kamar (pintu masuk)
Note on C9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Menghadap luar lambung kapal
Note on C11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian atas
Note on C12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian atas
Note on C13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian bawah
Note on C14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: peralatan
Note on D6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo tidak bersebelahan dengan sumber panas kasih insulasi key 5,6, 10
Note on D7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo tidak bersebelahan dengan sumber panas kasih insulasi key 5,6, 10
Note on D9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on I8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on I11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: karena permukaan horizontal terpapar suhu lingkungan maka suhu yang dipake 145 sesuai tabel 3-3
Note on I12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: karena permukaan horizontal terpapar suhu lingkungan maka suhu yang dipake 145 sesuai tabel 3-3
Note on I13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on L10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A X Gsf Nilai Gsf didapat dari tabel 3-3 single boundaries
Note on L14: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L15: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L16: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jumlah orang x beban latent Beban sensibel di tabel 3-8 all other sesuai suhu dalam ruangan
Note on M20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jumlah orang x beban latent Beban laten di tabel 3-8 all other sesuai suhu dalam ruangan

## Electrician
H | U | D |  |  |  | 1 m = | 3.28 | ft
SPACE |  | SPACE NO. |  | MAIN DECK |  | FRAMES | SPACE TEMP COOLING |  |  |  | 78.8 | °F | SPACE TEMP HEATING |  | 70 | °F
Electrician |  | MD/SB/4 |  |  |  | 16 to 20 | [10 empty] | Kondisi Temperature udara yang didesain. | 26°C | 78,8°F
ADJOINING SPACE | LOAD | INSUL | U | DIMENSION (m2) |  | AREA (Ft ²) | TO | TD | U | QS | QL | QT | TO | TD | U | Qw
| KEY | TYPE | KEY | Panjang | Tinggi/Lebar
Depan = Second Engineer Room | 4 | 10 | H | 3.41 | 2.4 | 88.0918 | TO: 78.8; TD: 0; U: 0.361; QS: 0; QT: 0
Belakang = Musholla | 5 | 10 | H | 3.41 | 2.4 | 88.0918 | TO: 78.8; TD: 0; U: 0.361; QS: 0; QT: 0 |  |  |  | Glass Solar Factor | saya pakai | 95F |  | Equipment
Kanan = Outdoor/Starboard Weather | 6 | 54 | H | 3 | 3.41 | 110.1147 | TO: 95; TD: 16.2; U: 0.196; QS: 349.6362; QT: 349.6362
Kiri = Gangway | 3 | 54 | H | 3 | 3.41 | 110.1147 | TO: 80; TD: 1.2; U: 0.191; QS: 25.2383; QT: 25.2383
Solar (window) | 3 |  | GLASS |  | 0.4 | 1.3519 | QS: 216.3105; QT: 216.3105
atas = Medical Room | 1 | 10 | D | 1.6 | 3.41 | 43.2278 | TO: 78.8; TD: 0; U: 0.272; QS: 0; QT: 0
atas = Chief Officerl Room | 1 | 10 | D | 1.4 | 3.41 | 51.3869 | TO: 78.8; TD: 0; U: 0.272; QS: 0; QT: 0 | [8 empty] | ql = q ,dl ×U F
atas = Toilet Medical Room | 1 | 54 | D | 1.2 | 1.2 | 15.5 | TO: 85; TD: 6.2; U: 0.169; QS: 16.2409; QT: 16.2409
bawah = Pumpman (2p) Room | 2 | 10 | U | 3 | 3.41 | 110.1147 | TO: 78.8; TD: 0; U: 0.435; QS: 0; QT: 0
lampu | 7 |  |  | 3 | 3.41 | 110.1147 | QS: 440.4588; QT: 440.4588 | [8 empty] | qs = q ,ds ×U F × H F
Udara Luar
Equipment : | 8
Handphone (15 Watt) | 8 | [5 empty] | QS: 51.1815 | [8 empty] | Jika tudung buang dipasang di atas peralatan, gunakan Faktor Tudung, H.F., 0,5. Beban laten untuk peralatan tersebut dianggap nol. Gunakan H.F. = 1,0 dalam Persamaan 3-6 ketika tudung buang tidak dipasang di atas peralatan. Lihat Tabel 3-6 untuk Faktor Penggunaan yang direkomendasikan, U.F
Personel
manusia (latent & sensibel) | 9 | [5 empty] | QS: 300; QL: 500; QT: 800 | Pemilihan Insulation
TOTAL HEAT | [6 empty] | QS: 1399.0661; QL: 500; QT: 1899.0661 |  |  |  | Lighting Loads
q=A x LC
Occupancy
ΔT = | 25 | °F | Vol. = |  | 867.0465 | Ft³ | TO: Out. Air =; TD: 15; U: cfm; QL: `
NOTES : GLASS SOLAR LOAD = 160 BTU/HR/ft² x 8,79 ft² = BTU/HR
SHF (Sensible Heat factor)= | Qs/Qt = | 0.73671 |  |  | Q = | Qs/1.08 x ΔT | TO: 51.8173; TD: use; U: 52; QS: Cfm
Min. Out. Air (1) Occupancy = | 1 | 15 | 15 | (2) R/C = | 28.9016 |  | TO: (3) Exhaust throuht Rad. Equip. =; QL: -; TO: HULL or JOB Numnber :
Check by : GEK/MAM
KEY |  | SYMBOLS |  |  |  |  | TO: SUMMARY; TO: Calculated by : Vieri Pramudya Dirgantara
1 = Deck Over |  | Qs = Heat Load, BTU/Hr, Sensible |  |  |  |  | TO: Sq. Ft.; TD: 728.1089; QS: ƩQL; QL: 500; TO: HEATING & COOLING LOAD CALCULATIONS |  |  |  | Heat Gain Personal
2 = Deck Under |  | QL = Heat Load, BTU/Hr, Latent |  |  |  |  | TO: Height; TD: 2.5; QS: ƩQT; QL: 1899.0661 | [10 empty] | Hunian Udara luar ruangan minimum berdasarkan hunian kamar adalah 12 CFM / orang untuk ruang hunian tinggi (misalnya, ruang rekreasi, ruang makan dan kamar mess) dan 15 CFM / orang untuk ruang ber-AC dengan hunian rendah (misalnya, kabin dan kantor). Tarif ini hanya akan ditingkatkan untuk mencapai keseimbangan udara dalam setiap subdivisi, tetapi tidak boleh melebihi 50 CFM / orang.
3 = Outboard Bhd or Shell |  | QT = Heat Load, BTU/Hr, Total |  |  |  |  | TO: Volume; TD: 867.0465; QS: Q; QL: 52
4 = Forward Bulkhead |  | QW = Heat Load, BTU/Hr, Winter |  |  |  |  | TO: R or C; TD: 28.9016
5 = After Bulkhead |  | U = Transmittance, BTU/Sq. Ft. Hr. °F |  |  |  |  | TO: ƩQs; TD: 1399.0661
6 = Inboard Bulkhead |  | TD = Temperature Differences |  |  |  |  | TO: SHF; TD: 0.73671; TO: REV; U: SHEET NO OF
7 = Lights |  | TO = Temp of Adjoining Space or Outside
8 = Equipment
9= Personnel
Kode | [6 empty] | U: Uk.Jendela; QL: 400; QT: mm; TO: 0.4; TD: m
10 | Tidak mengalami perpindahan panas | [25 empty] | Infiltrasi Untuk ruang seperti Ruang Kemudi (Rumah Percontohan) dengan pintu yang terbuka langsung ke cuaca, laju perubahan udara luar ruangan minimum adalah 60 menit, tetapi tidak boleh melebihi 50 CFM / orang.
54 | Mengalami perpindahan panas | [5 empty] | TO: Volume Ruangan
[7 empty] | p | 3
[7 empty] | l | 3.41
[7 empty] | t | 2.4 | [5 empty] | H | U | D
[8 empty] | 24.552 | m3
[8 empty] | 867.0465 | ft3
[6 empty] | 1 Watt= | TO: 3.4121; TD: BTU/hr
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Yang menghadap depan kapal
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Yang menghadap belakang kapal
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Depan kamar (pintu masuk)
Note on C9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Menghadap luar lambung kapal
Note on C11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian atas
Note on C12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian atas
Note on C14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian bawah
Note on C15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: peralatan
Note on D6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo tidak bersebelahan dengan sumber panas kasih insulasi key 5,6, 10
Note on D7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo tidak bersebelahan dengan sumber panas kasih insulasi key 5,6, 10
Note on D9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on I8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on I11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: karena permukaan horizontal terpapar suhu lingkungan maka suhu yang dipake 145 sesuai tabel 3-3
Note on I12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: karena permukaan horizontal terpapar suhu lingkungan maka suhu yang dipake 145 sesuai tabel 3-3
Note on I14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on L10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A X Gsf Nilai Gsf didapat dari tabel 3-3 single boundaries
Note on L15: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L16: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jumlah orang x beban latent Beban sensibel di tabel 3-8 all other sesuai suhu dalam ruangan
Note on M20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jumlah orang x beban latent Beban laten di tabel 3-8 all other sesuai suhu dalam ruangan

## Second Engineer
H | U | D |  |  |  | 1 m = | 3.28 | ft
SPACE |  | SPACE NO. |  | MAIN DECK |  | FRAMES | SPACE TEMP COOLING |  |  |  | 78.8 | °F | SPACE TEMP HEATING |  | 70 | °F
Second Engineer |  | MD/SB/4 |  |  |  | 20 to 25 | [10 empty] | Kondisi Temperature udara yang didesain. | 26°C | 78,8°F
ADJOINING SPACE | LOAD | INSUL | U | DIMENSION (m2) |  | AREA (Ft ²) | TO | TD | U | QS | QL | QT | TO | TD | U | Qw
| KEY | TYPE | KEY | Panjang | Tinggi/Lebar
Depan = Outdoor/Solar | 4 | 54 | H | 3.4 | 2.4 | 87.8334 | TO: 125; TD: 46.2; U: 0.212; QS: 860.2757; QT: 860.2757
Belakang = Electrician Room | 5 | 10 | H | 3.4 | 2.4 | 87.8334 | TO: 78.8; TD: 0; U: 0.361; QS: 0; QT: 0 |  |  |  | Glass Solar Factor | saya pakai | 95F |  | Equipment
Kanan = Outdoor/Starboard Weather | 6 | 54 | H | 3 | 2.4 | 77.5001 | TO: 95; TD: 16.2; U: 0.196; QS: 246.0783; QT: 246.0783
Kiri = Gangway | 3 | 54 | H | 3 | 3.4 | 109.7918 | TO: 80; TD: 1.2; U: 0.191; QS: 25.1643; QT: 25.1643
Solar (window) | 3 |  | GLASS |  | 0.4 | 1.3519 | QS: 216.3105; QT: 216.3105
atas = Chief Officer Room | 1 | 10 | D | 3 | 3.4 | 94.2918 | TO: 78.8; TD: 0; U: 0.272; QS: 0; QT: 0
atas = Toilet Chief Officer Room | 1 | 54 | D | 1.2 | 1.2 | 15.5 | TO: 85; TD: 6.2; U: 0.169; QS: 16.2409; QT: 16.2409 | [8 empty] | ql = q ,dl ×U F
bawah = Fireman (2p) Room | 2 | 10 | U | 3 | 3.4 | 109.7918 | TO: 78.8; TD: 0; U: 0.435; QS: 0; QT: 0
lampu | 7 |  |  | 3 | 3.4 | 109.7918 | QS: 439.1671; QT: 439.1671
qs = q ,ds ×U F × H F
Udara Luar
Equipment : | 8
Handphone (15 Watt) | 8 | [5 empty] | QS: 51.1815 | [8 empty] | Jika tudung buang dipasang di atas peralatan, gunakan Faktor Tudung, H.F., 0,5. Beban laten untuk peralatan tersebut dianggap nol. Gunakan H.F. = 1,0 dalam Persamaan 3-6 ketika tudung buang tidak dipasang di atas peralatan. Lihat Tabel 3-6 untuk Faktor Penggunaan yang direkomendasikan, U.F
Personel
manusia (latent & sensibel) | 9 | [5 empty] | QS: 300; QL: 500; QT: 800 | Pemilihan Insulation
TOTAL HEAT | [6 empty] | QS: 2154.4182; QL: 500; QT: 2654.4182 |  |  |  | Lighting Loads
q=A x LC
Occupancy
ΔT = | 25 | °F | Vol. = |  | 867.0465 | Ft³ | TO: Out. Air =; TD: 15; U: cfm; QL: `
NOTES : GLASS SOLAR LOAD = 160 BTU/HR/ft² x 8,79 ft² = BTU/HR
SHF (Sensible Heat factor)= | Qs/Qt = | 0.81163 |  |  | Q = | Qs/1.08 x ΔT | TO: 79.7933; TD: use; U: 80; QS: Cfm
Min. Out. Air (1) Occupancy = | 1 | 15 | 15 | (2) R/C = | 28.9016 |  | TO: (3) Exhaust throuht Rad. Equip. =; QL: -; TO: HULL or JOB Numnber :
Check by : GEK/MAM
KEY |  | SYMBOLS |  |  |  |  | TO: SUMMARY; TO: Calculated by : Vieri Pramudya Dirgantara
1 = Deck Over |  | Qs = Heat Load, BTU/Hr, Sensible |  |  |  |  | TO: Sq. Ft.; TD: 693.686; QS: ƩQL; QL: 500; TO: HEATING & COOLING LOAD CALCULATIONS |  |  |  | Heat Gain Personal
2 = Deck Under |  | QL = Heat Load, BTU/Hr, Latent |  |  |  |  | TO: Height; TD: 2.5; QS: ƩQT; QL: 2654.4182 | [10 empty] | Hunian Udara luar ruangan minimum berdasarkan hunian kamar adalah 12 CFM / orang untuk ruang hunian tinggi (misalnya, ruang rekreasi, ruang makan dan kamar mess) dan 15 CFM / orang untuk ruang ber-AC dengan hunian rendah (misalnya, kabin dan kantor). Tarif ini hanya akan ditingkatkan untuk mencapai keseimbangan udara dalam setiap subdivisi, tetapi tidak boleh melebihi 50 CFM / orang.
3 = Outboard Bhd or Shell |  | QT = Heat Load, BTU/Hr, Total |  |  |  |  | TO: Volume; TD: 867.0465; QS: Q; QL: 80
4 = Forward Bulkhead |  | QW = Heat Load, BTU/Hr, Winter |  |  |  |  | TO: R or C; TD: 28.9016
5 = After Bulkhead |  | U = Transmittance, BTU/Sq. Ft. Hr. °F |  |  |  |  | TO: ƩQs; TD: 2154.4182
6 = Inboard Bulkhead |  | TD = Temperature Differences |  |  |  |  | TO: SHF; TD: 0.81163; TO: REV; U: SHEET NO OF
7 = Lights |  | TO = Temp of Adjoining Space or Outside
8 = Equipment
9= Personnel
Kode | [6 empty] | U: Uk.Jendela; QL: 400; QT: mm; TO: 0.4; TD: m
10 | Tidak mengalami perpindahan panas | [25 empty] | Infiltrasi Untuk ruang seperti Ruang Kemudi (Rumah Percontohan) dengan pintu yang terbuka langsung ke cuaca, laju perubahan udara luar ruangan minimum adalah 60 menit, tetapi tidak boleh melebihi 50 CFM / orang.
54 | Mengalami perpindahan panas | [5 empty] | TO: Volume Ruangan
[7 empty] | p | 3
[7 empty] | l | 3.41
[7 empty] | t | 2.4 | [5 empty] | H | U | D
[8 empty] | 24.552 | m3
[8 empty] | 867.0465 | ft3
[6 empty] | 1 Watt= | TO: 3.4121; TD: BTU/hr
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Yang menghadap depan kapal
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Yang menghadap belakang kapal
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Depan kamar (pintu masuk)
Note on C9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Menghadap luar lambung kapal
Note on C13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian bawah
Note on C14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: peralatan
Note on D6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo tidak bersebelahan dengan sumber panas kasih insulasi key 5,6, 10
Note on D7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo tidak bersebelahan dengan sumber panas kasih insulasi key 5,6, 10
Note on D9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on I8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on I13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on L10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A X Gsf Nilai Gsf didapat dari tabel 3-3 single boundaries
Note on L14: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L15: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L16: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jumlah orang x beban latent Beban sensibel di tabel 3-8 all other sesuai suhu dalam ruangan
Note on M20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jumlah orang x beban latent Beban laten di tabel 3-8 all other sesuai suhu dalam ruangan

## Smoking Room
H | U | D |  |  |  | 1 m = | 3.28 | ft
SPACE |  | SPACE NO. |  | MAIN DECK |  | FRAMES | SPACE TEMP COOLING |  |  |  | 78.8 | °F | SPACE TEMP HEATING |  | 70 | °F
Smoking Room |  | MD/SB/4 |  |  |  | 20 to 25 | [10 empty] | Kondisi Temperature udara yang didesain. | 26°C | 78,8°F
ADJOINING SPACE | LOAD | INSUL | U | DIMENSION (m2) |  | AREA (Ft ²) | TO | TD | U | QS | QL | QT | TO | TD | U | Qw
| KEY | TYPE | KEY | Panjang | Tinggi/Lebar
Depan = Outdoor/Solar | 4 | 54 | H | 4 | 2.4 | 103.3334 | TO: 125; TD: 46.2; U: 0.212; QS: 1012.089; QT: 1012.089
Belakang = Gangway | 5 | 54 | H | 4 | 2.4 | 103.3334 | TO: 80; TD: 1.2; U: 0.191; QS: 23.684; QT: 23.684 |  |  |  | Glass Solar Factor | saya pakai | 95F |  | Equipment
Kanan = Gangway | 6 | 54 | H | 3.5 | 2.4 | 90.4168 | TO: 80; TD: 1.2; U: 0.191; QS: 20.7235; QT: 20.7235
Kiri = Gangway | 3 | 54 | H | 3.5 | 3.4 | 128.0904 | TO: 80; TD: 1.2; U: 0.191; QS: 29.3583; QT: 29.3583
Solar (window) | 3 |  | GLASS |  | 0.4 | 2.7039 | QS: 432.6209; QT: 432.6209
atas = Chief Officer & Engineer Office | 1 | 10 | D | 3.5 | 4 | 150.6946 | TO: 78.8; TD: 0; U: 0.272; QS: 0; QT: 0
bawah = Dry Provision Room | 2 | 54 | U | 3 | 4 | 129.1668 | TO: 110; TD: 31.2; U: 0.207; QS: 834.2109; QT: 834.2109 | [8 empty] | ql = q ,dl ×U F
bawah = Gangway | 2 | 54 | U | 0.5 | 4 | 21.5278 | TO: 80; TD: 1.2; U: 0.207; QS: 5.3475; QT: 5.3475
lampu | 7 |  |  | 3.5 | 4 | 150.6946 | QS: 1054.8622; QT: 1054.8622
qs = q ,ds ×U F × H F
Udara Luar
Equipment : | 8
Jika tudung buang dipasang di atas peralatan, gunakan Faktor Tudung, H.F., 0,5. Beban laten untuk peralatan tersebut dianggap nol. Gunakan H.F. = 1,0 dalam Persamaan 3-6 ketika tudung buang tidak dipasang di atas peralatan. Lihat Tabel 3-6 untuk Faktor Penggunaan yang direkomendasikan, U.F
Personel
manusia (latent & sensibel) | 9 | [5 empty] | QS: 1200; QL: 2000; QT: 3200 | Pemilihan Insulation
TOTAL HEAT | [6 empty] | QS: 4612.8964; QL: 2000; QT: 6612.8964 |  |  |  | Lighting Loads
q=A x LC
Occupancy
ΔT = | 25 | °F | Vol. = |  | 1186.5739 | Ft³ | TO: Out. Air =; TD: 60; U: cfm; QL: `
NOTES : GLASS SOLAR LOAD = 160 BTU/HR/ft² x 8,79 ft² = BTU/HR
SHF (Sensible Heat factor)= | Qs/Qt = | 0.69756 |  |  | Q = | Qs/1.08 x ΔT | TO: 170.848; TD: use; U: 171; QS: Cfm
Min. Out. Air (1) Occupancy = | 4 | 15 | 60 | (2) R/C = | 39.5525 |  | TO: (3) Exhaust throuht Rad. Equip. =; QL: -; TO: HULL or JOB Numnber :
Check by : GEK/MAM
KEY |  | SYMBOLS |  |  |  |  | TO: SUMMARY; TO: Calculated by : Vieri Pramudya Dirgantara
1 = Deck Over |  | Qs = Heat Load, BTU/Hr, Sensible |  |  |  |  | TO: Sq. Ft.; TD: 879.9617; QS: ƩQL; QL: 2000; TO: HEATING & COOLING LOAD CALCULATIONS |  |  |  | Heat Gain Personal
2 = Deck Under |  | QL = Heat Load, BTU/Hr, Latent |  |  |  |  | TO: Height; TD: 2.5; QS: ƩQT; QL: 6612.8964 | [10 empty] | Hunian Udara luar ruangan minimum berdasarkan hunian kamar adalah 12 CFM / orang untuk ruang hunian tinggi (misalnya, ruang rekreasi, ruang makan dan kamar mess) dan 15 CFM / orang untuk ruang ber-AC dengan hunian rendah (misalnya, kabin dan kantor). Tarif ini hanya akan ditingkatkan untuk mencapai keseimbangan udara dalam setiap subdivisi, tetapi tidak boleh melebihi 50 CFM / orang.
3 = Outboard Bhd or Shell |  | QT = Heat Load, BTU/Hr, Total |  |  |  |  | TO: Volume; TD: 1186.5739; QS: Q; QL: 171
4 = Forward Bulkhead |  | QW = Heat Load, BTU/Hr, Winter |  |  |  |  | TO: R or C; TD: 39.5525
5 = After Bulkhead |  | U = Transmittance, BTU/Sq. Ft. Hr. °F |  |  |  |  | TO: ƩQs; TD: 4612.8964
6 = Inboard Bulkhead |  | TD = Temperature Differences |  |  |  |  | TO: SHF; TD: 0.69756; TO: REV; U: SHEET NO OF
7 = Lights |  | TO = Temp of Adjoining Space or Outside
8 = Equipment
9= Personnel
Kode | [6 empty] | U: Uk.Jendela; QL: 400; QT: mm; TO: 0.4; TD: m
10 | Tidak mengalami perpindahan panas | [5 empty] | U: Jumlah Jendela; QL: 2 | [10 empty] | Infiltrasi Untuk ruang seperti Ruang Kemudi (Rumah Percontohan) dengan pintu yang terbuka langsung ke cuaca, laju perubahan udara luar ruangan minimum adalah 60 menit, tetapi tidak boleh melebihi 50 CFM / orang.
54 | Mengalami perpindahan panas | [5 empty] | TD: Volume Ruangan
[7 empty] | p | 3.5
[7 empty] | l | 4
[7 empty] | t | 2.4 | [5 empty] | H | U | D
[8 empty] | 33.6 | m3
[8 empty] | 1186.5739 | ft3
[6 empty] | 1 Watt= | TO: 3.4121; TD: BTU/hr
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Yang menghadap depan kapal
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Yang menghadap belakang kapal
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Depan kamar (pintu masuk)
Note on C9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Menghadap luar lambung kapal
Note on C12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian bawah
Note on C13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bagian bawah
Note on C14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lampu
Note on C17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: peralatan
Note on D6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo tidak bersebelahan dengan sumber panas kasih insulasi key 5,6, 10
Note on D7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo tidak bersebelahan dengan sumber panas kasih insulasi key 5,6, 10
Note on D9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on D13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Kalo bersebelahan dengan sumber panas kasih insulasi key 55, 62, 63
Note on I8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on I12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on I13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tabel 3-2
Note on L10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A X Gsf Nilai Gsf didapat dari tabel 3-3 single boundaries
Note on L14: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L15: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L16: Invinandriii: LC X A. LC didapat dari tabel 3-4
Note on L20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jumlah orang x beban latent Beban sensibel di tabel 3-8 all other sesuai suhu dalam ruangan
Note on M20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jumlah orang x beban latent Beban laten di tabel 3-8 all other sesuai suhu dalam ruangan