## SUMMARY
TOTAL JUMLAH RUANGAN yg DIKONDISIKAN
Nama Kapal : | MTM Antwerp
Jenis Kapal : | Product Oil Tanker
Nama Mahasiswa : | Daffa Gabillah Maulana Gapur
NRP : | 0322040051
No | Room Name | Jumlah Ruangan
1 | Main Deck | 4
2 | Poop Deck | 8
3 | A Deck | 10
4 | B Deck | 10
5 | C Deck | 11
6 | Bridge Deck | 1

## MAIN DK
List Ruangan yg Perlu Dikondisikan dengan Sistem Air Handling Unit (AHU)
No | Room Name | Dimension in Meter |  |  | Area [ft2] | Volume [ft3] | Cooling Capacity [Btu/hr]
|  | Length | Width | Height
1 | Vegetable Store | 5.6 | 2.8 | 3 | 165.1974 | 1463.3633 | 637.925
2 | Meat/Fish Store | 4.2 | 2.8 | 3 | 113.0209 | 1001.1699
3 | Engine Control Room | 5 | 10.7 | 3 | 704.9278 | 6244.4395
4 | Dry Provision Store | 10.9 | 3.55 | 3 | 519.6682 | 4603.36
4 | Total Jumlah Ruangan

## POOP DK
List Ruangan yg Perlu Dikondisikan dengan Sistem Air Handling Unit (AHU)
No | Room Name | Dimension in Meter |  |  | Area [ft2] | Volume [ft3] | Cooling Capacity [Btu/hr]
|  | Length | Width | Height
1 | Cargo Control Room | 5.55 | 3.9 | 2.7 | 254.8892 | 2257.8764 | 214.8769
2 | Ship Office | 5.5 | 4.95 | 2.7 | 318.3962 | 2820.4385
3 | Deck Change Room | 2.2 | 2.6 | 2.7 | 67.1667 | 594.9809
4 | Store | 2.2 | 0.95 | 2.7 | 31 | 274.6066
5 | Galley | 6.1 | 6 | 2.7 | 300.5281 | 2662.1583
6 | Pantry | 5.3 | 2.8 | 2.7 | 14.84 | 40.068
7 | Crew Mess | 7.6 | 6 | 2.7 | 404.2921 | 3581.3276
8 | Office Mess | 5.5 | 6.2 | 2.7 | 392.4518 | 3476.4432
8 | Total Jumlah Ruangan

## A DK
List Ruangan yg Perlu Dikondisikan dengan Sistem Air Handling Unit (AHU)
No | Room Name | Dimension in Meter |  |  | Area [ft2] | Volume [ft3] | Cooling Capacity
|  | Length | Width | Height
1 | Motorman 2 Cabin | 4.45 | 3 | 2.7 | 139.5001 | 1235.7297
2 | Motorman 1 Cabin | 4.45 | 3 | 2.7 | 134.2258 | 1189.0084
3 | AB 2 Cabin | 4.9 | 3.3 | 2.7 | 156.3995 | 1385.4284
4 | AB 1 Cabin | 3.4 | 4.8 | 2.7 | 154.462 | 1368.2655
5 | Hospital | 3.2 | 6 | 2.7 | 185.0314 | 1639.0581
6 | OS Cabin | 4.45 | 3 | 2.7 | 134.2258 | 1189.0084
7 | Messman Cabin | 4.45 | 3 | 2.7 | 134.2258 | 1189.0084
8 | Fitter Cabin | 4.45 | 3 | 2.7 | 144.7745 | 1282.4509
9 | Suez Crew Room | 5.3 | 2.9 | 2.7 | 145.5279 | 1289.1254
10 | Hospital Bath Room | 1.3 | 2.2 | 2.7 | 38.75 | 343.2582
10 | Total Jumlah Ruangan

## B DK
List Ruangan yg Perlu Dikondisikan dengan Sistem Air Handling Unit (AHU)
No | Room Name | Dimension in Meter |  |  | Area [ft2] | Volume [ft3] | Cooling Capacity
|  | Length | Width | Height
1 | 2nd Engineer Cabin | 4.2 | 6.15 | 2.7 | 242.7259 | 2150.1315
2 | 3rd Engineer Cabin | 3.35 | 5 | 2.7 | 162.8578 | 1442.6381
3 | Electrician Crew Cabin | 3.35 | 5 | 2.7 | 38.75 | 343.2582
4 | Bosun Crew Cabin | 3.35 | 5 | 2.7 | 168.3474 | 1491.2664
5 | Owner Cabin | 4.2 | 5.25 | 2.7 | 242.7259 | 2150.1315
6 | Gym Room | 2.15 | 2.65 | 2.7 | 889.8167 | 7882.2344
7 | 2nd Officer Cabin | 4.2 | 6.15 | 2.7 | 234.1148 | 2073.8519
8 | 3rd Officer Cabin | 3.35 | 5 | 2.7 | 162.8578 | 1442.6381
9 | Pumpman Cabin | 3.35 | 5 | 2.7 | 162.8578 | 1442.6381
10 | Cook Crew Cabin | 3.35 | 5 | 2.7 | 168.3474 | 1491.2664
10 | Total Jumlah Ruangan

## C DK
List Ruangan yg Perlu Dikondisikan dengan Sistem Air Handling Unit (AHU)
No | Room Name | Dimension in Meter |  |  | Area [ft2] | Volume [ft3] | Cooling Capacity
|  | Length | Width | Height
1 | Captain Cabin | 5.5 | 3.2 | 2.7 | 206.8822 | 1832.6176
2 | Captain Bedroom | 2 | 3.45 | 2.7 | 86.7301 | 768.2787
3 | Chief Officer Cabin | 4.9651 | 3.7016 | 2.7 | 196.1183 | 1737.2681
4 | Chief Officer Bedroom | 2.0554 | 3.5503 | 2.7 | 89.9862 | 797.1219
5 | Pilot Cabin | 3.1766 | 4.9651 | 2.7 | 145.9585 | 1292.9394
6 | Office Room | 4.4223 | 7.1006 | 2.7 | 324.2625 | 2872.404
7 | Instrumentation Room | 3.6571 | 2.8563 | 2.7 | 107.639 | 953.4951
8 | 1st Engineer Cabin | 3.7016 | 4.9651 | 2.7 | 196.1183 | 1737.2681
9 | 1st Engineer Bedroom | 2.0821 | 3.5503 | 2.7 | 89.9862 | 797.1219
10 | Chief Engineer Cabin | 4.5736 | 6.1129 | 2.7 | 206.8822 | 1832.6176
11 | Chief Engineer Bedroom | 2.1088 | 3.5236 | 2.7 | 86.7301 | 768.2787
11 | Total Jumlah Ruangan

## BRIDGE DK
List Ruangan yg Perlu Dikondisikan dengan Sistem Air Handling Unit (AHU)
No | Room Name | Dimension in Meter |  |  | Area [ft2] | Volume [ft3] | Cooling Capacity
|  | Length | Width | Height
1 | Wheel House | 11.2382 | 22.4675 | 2.9 | 1883.5749 | 16685.2109
1 | Total Jumlah Ruangan

## VEGETABLE STORE
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
VEGETABLE STORE |  | 4001 |  | MAIN DECK | -8 - 2
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
ELECTRICIAN WORKSHOP | 6 | 0"-0 | H | 5.4812 m x 3 m | 176.9973 | 78 | 105 | 27 | 0.93 | ↔ | 4444.4014 |  | 4444.4014 | 78 | 78 | 0 | 0.93 | ↔ | 0
MEAT/FISH STORE | 6 | 0"-0 | H | 2.8 m x 3 m | 90.4168 | 78 | 78 | 0 | 0.93 | ↔ | 0 |  | 0 | 78 | 40 | 38 | 0.93 | ↔ | 3195.3283
DRY PROVISION STORE | 6 | 0"-6 | H | 5.4812 m x 3 m | 176.9973 | 78 | 78 | 0 | 0.313 | ↔ | 0 |  | 0 | 78 | 78 | 0 | 0.313 | ↔ | 0
TECH. FW TK | 2 | 0"-0 | D | 5.4812 m x 2.8 m | 165.1974 | 78 | 120 | 42 | 0.801 | ↓ | 5557.5726 |  | 5557.5726 | 78 | 78 | 0 | 0.801 | ↓ | 0
OUTDOOR SPACE | 3 | 0"-0 | U | 5.4812 m x 2.8 m | 165.1974 | 78 | 95 | 17 | 1.491 | ↑ | 4187.2597 |  | 4187.2597 | 78 | 78 | 0 | 1.491 | ↑ | 0
OUTDOOR SPACE | 3 | 0"-0 | H | 2.8 m x 3 m | 90.4168 | 78 | 95 | 17 | 1.32 | ↔ | 2028.9521 |  | 2028.9521 | 78 | 78 | 0 | 1.32 | ↔ | 0
TRANSMISSION SUBTOTAL | [12 empty] | 16218.1857 | [5 empty] | 3195.3283
WINDOW | 8 |  |  |  | 0 | [5 empty] | 0 |  | 0
LIGHTS | 7 |  |  |  | 165.1974 | [5 empty] | 660.7898 |  | 660.7898
EQUIPMENT | 8 | [11 empty] | 0
FOOD | [10 empty] | 30 | 30 | 60
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
TOTAL HEAT | [12 empty] | 17738.9755 | [5 empty] | 3195.3283
TOTAL HEAT | [5 empty] | 20934.3038
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 165.1974 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1463.3633 | cb. ft
|  |  |  | R of C | 48.7788 | CFM
|  |  |  | qS TOTAL | 17223.9755 | Btu/hr
|  |  |  | qL TOTAL | 515 | Btu/hr
|  |  |  | qT TOTAL | 17738.9755 | Btu/hr
|  |  |  | qW TOTAL | 3195.3283 | Btu/hr
|  |  |  | Q | 637.925 | CFM
|  |  |  | CFM | 638 | CFM
|  |  |  | Q (kW) | 0.18698 | kW
|  |  |  | SHF | 0.97097
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## MEET FISH STORE
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 40 F | [7 empty] | SPACE TEMP HEATING 40 F
MEAT/FISH STORE |  | 4002 |  | MAIN DECK
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
VEGETABLE STORE | 6 | 6"-150 | H | 2.8 m x 3 m | 90.4168 | 40 | 78 | 38 | 0.063 | ↔ | 216.4577 |  | 216.4577 | 40 | 40 | 0 | 0.1 | ↔ | 0
VENTILATION DUCT SPACE | 6 | 3"-94 | H | 0.7 m x 3 m + 1.8 m x 3 m | 80.7292 | 40 | 120 | 80 | 0.158 | ↔ | 1020.4177 |  | 1020.4177 | 40 | 40 | 0 | 0.1 | ↔ | 0
DRY PROVISION STORE | 6 | 0"-6 | H | 3.6 m x 3 m | 116.2501 | 40 | 78 | 38 | 0.313 | ↔ | 1382.6789 |  | 1382.6789 | 40 | 40 | 0 | 0.1 | ↔ | 0
ENGINE ROOM | 6 | 3"-94 | H | 2.4 m x 3 m | 77.5001 | 40 | 130 | 90 | 0.158 | ↔ | 1102.0511 |  | 1102.0511 | 40 | 40 | 0 | 0.1 | ↔ | 0
WC | 6 | 0"-6 | H | 2.1 m x 3 m | 67.8126 | 40 | 85 | 45 | 0.313 | ↔ | 955.14 |  | 955.14 | 40 | 40 | 0 | 0.1 | ↔ | 0
NO. 3 HFO STORE TANK | 2 | 3"-94 | H | 2.4 m x 0.7 m + 4.2 m x 2.1 m | 113.0209 | 40 | 120 | 80 | 0.158 | ↓ | 1428.5848 |  | 1428.5848 | 40 | 40 | 0 | 0.1 | ↓ | 0
OUTDOOR SPACE | 1 | 0"-6 | H | 1.4 m x 4.2 m | 63.2917 | 40 | 95 | 55 | 0.313 | ↑ | 1089.5672 |  | 1089.5672 | 40 | 40 | 0 | 0.1 | ↑ | 0
SAFETY EQUIPMENT STATION | 1 | 3"-94 | D | 1.4 m x 4.2 m | 63.2917 | 40 | 110 | 70 | 0.144 | ↑ | 637.9807 |  | 637.9807 | 40 | 40 | 0 | 0.1 | ↑ | 0
VENTILATION SPACE | 1 | 3"-94 | D | 1.8 m x 0.7 m | 13.5625 | 40 | 120 | 80 | 0.144 | ↑ | 156.2402 |  | 156.2402 | 40 | 40 | 0 | 0.1 | ↑ | 0
TRANSMISSION SUBTOTAL | [12 empty] | 7989.1184 | [5 empty] | 0
LIGHTS | 7 |  |  |  | 113.0209 | [5 empty] | 452.0838 |  | 452.0838
EQUIPMENT | 8
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
TOTAL HEAT | [12 empty] | 9241.2022 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 9241.2022
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 113.0209 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1001.1699 | cb. ft
|  |  |  | R of C | 33.3723 | CFM
|  |  |  | qS TOTAL | 8756.2022 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 9241.2022 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 324.3038 | CFM
|  |  |  | CFM | 325 | CFM
|  |  |  | Q (kW) | 0.095248 | kW
|  |  |  | SHF | 0.94752
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## DRY PROVISION STORE
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
DRY PROVIISION STORE |  | 4003 |  | MAIN DECK | -9 ~ 13
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 3"-94 | H | 1.1 m x 3 m | 399.0608 | 78 | 105 | 27 | 0.158 | ↔ | 1702.3935 |  | 1702.3935 | 70 | 70 | 0 | 0.158 | ↔ | 0
LINEN ROOM | 6 | 3"-94 | H | 2.3776 m x 3 m | 212.1134 | 78 | 105 | 27 | 0.158 | ↔ | 904.8758 |  | 904.8758 | 70 | 70 | 0 | 0.158 | ↔ | 0
ENGINE CHANGE ROOM | 6 | 3"-94 | H | 1.6 m x 3 m | 287.6114 | 78 | 105 | 27 | 0.158 | ↔ | 1226.9503 |  | 1226.9503 | 70 | 70 | 0 | 0.158 | ↔ | 0
WC | 6 | 3"-94 | H | 1.6 m x 3 m | 75.498 | 78 | 85 | 7 | 0.158 | ↔ | 83.5008 |  | 83.5008 | 70 | 70 | 0 | 0.158 | ↔ | 0
MEAT/FISH STORE | 6 | 0"-6 | H | 3.8 m x 3 m | 35.9514 | 78 | 78 | 0 | 0.313 | ↔ | 0 |  | 0 | 70 | 70 | 0 | 0.313 | ↔ | 0
VEGETABLE STORE | 6 | 0"-6 | H |  | 0 | 78 | 78 | 0 | 0.313 | ↔ | 0 |  | 0 | 70 | 70 | 0 | 0.313 | ↔ | 0
OUTDOOR SPACE | 3 | 3"-94 | H | (3.052 m + 14.5 m) x 3 m | 37.6736 | 78 | 95 | 17 | 0.158 | ↔ | 101.1914 |  | 101.1914 | 70 | 70 | 0 | 0.158 | ↔ | 0
OUTDOOR SPACE | 1 | 0"-0 | U |  | 519.6682 | 78 | 95 | 17 | 1.491 | ↑ | 13172.0292 |  | 13172.0292 | 70 | 70 | 0 | 1.491 | ↑ | 0
VOID COFFERDAM | 2 | 0"-0 | D |  | 63.7729 | 78 | 120 | 42 | 0.801 | ↓ | 2145.4472 |  | 2145.4472 | 70 | 70 | 0 | 0.801 | ↓ | 0
NO. 3 HFO STORAGE TANK (S) | 2 | 0"-0 | D |  | 207.1814 | 78 | 120 | 42 | 0.801 | ↓ | 6969.9965 |  | 6969.9965 | 70 | 70 | 0 | 0.801 | ↓ | 0
TECHNICAL FW TANK | 2 | 0"-0 | D |  | 248.18 | 78 | 120 | 42 | 0.801 | ↓ | 8349.272 |  | 8349.272 | 70 | 70 | 0 | 0.801 | ↓ | 0
TRANSMISSION SUBTOTAL | [12 empty] | 34655.6567 | [5 empty] | 0
WINDOW |  |  |  |  | 0 | [5 empty] | 0 |  | 0
LIGHTS | 7 |  |  |  | 519.6682 | [5 empty] | 6236.0181 |  | 6236.0181
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 41691.6748 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 41691.6748
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 519.6682 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 4603.36 | cb. ft
|  |  |  | R of C | 153.4453 | CFM
|  |  |  | qS TOTAL | 41206.6748 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 41691.6748 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 1526.1731 | CFM
|  |  |  | CFM | 1527 | CFM
|  |  |  | Q (kW) | 0.44752 | kW
|  |  |  | SHF | 0.98837
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## ENGINE CONTROL ROOM
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
ENGINE CONTROL ROOM |  | 4004 |  | MAIN DECK | 20 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
COFFERDAM | 3 | 4"-129 | H | 11.1 m x 3 m | 399.0608 | 78 | 120 | 42 | 0.063 | ↔ | 1055.915 |  | 1055.915 | 70 | 70 | 0 | 0.063 | ↔ | 0
VALVE CONTROL UNIT ROOM | 6 | 3"-94 | H | 5.9 m x 3 m | 212.1134 | 78 | 110 | 32 | 0.158 | ↔ | 1072.4454 |  | 1072.4454 | 70 | 70 | 0 | 0.158 | ↔ | 0
ENGINE ROOM | 6 | 3"-94 | H | (4.9 m + 3.1 m) x 3 m | 287.6114 | 78 | 130 | 52 | 0.158 | ↔ | 2363.0153 |  | 2363.0153 | 70 | 70 | 0 | 0.158 | ↔ | 0
STAIRWAY | 6 | 3"-94 | H | 2.1 m x 3 m | 75.498 | 78 | 105 | 27 | 0.171 | ↑ | 348.5742 |  | 348.5742 | 70 | 70 | 0 | 0.171 | ↑ | 0
SERVICE DUCT TRUNK | 6 | 3"-94 | H | 1 m x 3 m | 35.9514 | 78 | 120 | 42 | 0.144 | ↓ | 217.4342 |  | 217.4342 | 70 | 70 | 0 | 0.144 | ↓ | 0
FIRE/FOAM STATION | 6 | 3"-94 | H | 5.9 m x 3 m | 212.1134 | 78 | 110 | 32 | 0.144 | ↓ | 977.4186 |  | 977.4186 | 70 | 70 | 0 | 0.144 | ↓ | 0
PASSAGE WAY | 1 | 3"-94 | U | (1.3 m x 1 m) + (2.2 m * 1 m) | 37.6736 | 78 | 80 | 2 | 0.144 | ↓ | 10.85 |  | 10.85 | 70 | 70 | 0 | 0.144 | ↓ | 0
ENGINE ROOM | 2 | 3"-94 | D | 5.9 m x 6.45 m | 227.9256 | 78 | 130 | 52 | 0.144 | ↓ | 1706.7068 |  | 1706.7068 | 70 | 70 | 0 | 0.144 | ↓ | 0
HYDRAULIC AGREGATES ROOM | 2 | 0"-0 | D | 5.9 m x 4.65 m | 295.3076 | 78 | 110 | 32 | 0.801 | ↓ | 7569.3243 |  | 7569.3243 | 70 | 70 | 0 | 0.801 | ↓ | 0
G/E LO STORAGE TANK | 2 | 0"-0 | D | 2.4 m x 2.3 m | 59.4167 | 78 | 120 | 42 | 0.801 | ↓ | 1998.8976 |  | 1998.8976 | 70 | 70 | 0 | 0.801 | ↓ | 0
MGO SERVICE TANK | 2 | 0"-0 | D | 2.1 m x 3.2 m | 72.3334 | 78 | 120 | 42 | 0.801 | ↓ | 2433.4405 |  | 2433.4405 | 70 | 70 | 0 | 0.801 | ↓ | 0
MGO SETTLING TANK | 2 | 0"-0 | D | 1.45 m x 3.2 m | 49.9445 | 78 | 120 | 42 | 0.801 | ↓ | 1680.2327 |  | 1680.2327 | 70 | 70 | 0 | 0.801 | ↓ | 0
TRANSMISSION SUBTOTAL | [12 empty] | 21434.2547 | [5 empty] | 0
WINDOW |  |  |  |  | 0 | [5 empty] | 0 |  | 0
LIGHTS | 7 |  |  |  | 704.9278 | [5 empty] | 8459.1337 |  | 8459.1337
EQUIPMENT: Control Panels | 8 | [9 empty] | 9826.56 |  | 9826.56
EQUIPMENT: Computer Consoles | 8 | [9 empty] | 1944.84 |  | 1944.84
EQUIPMENT: UCS System | 8 | [9 empty] | 3684.96 |  | 3684.96
EQUIPMENT: Communication Equipment | 8 | [9 empty] | 614.16 |  | 614.16
PERSONNEL | 9 | [9 empty] | 945 | 1455 | 2400
INFILTRATION
TOTAL HEAT | [12 empty] | 48363.9084 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 48363.9084
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 704.9278 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 6244.4395 | cb. ft
|  |  |  | R of C | 208.148 | CFM
|  |  |  | qS TOTAL | 46908.9084 | Btu/hr
|  |  |  | qL TOTAL | 1455 | Btu/hr
|  |  |  | qT TOTAL | 48363.9084 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 1737.367 | CFM
|  |  |  | CFM | 1738 | CFM
|  |  |  | Q (kW) | 0.50936 | kW
|  |  |  | SHF | 0.96992
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## GALLEY
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
GALLEY |  | 5001 |  | POOP DECK | 16 ~ 24
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
OUTDOOR SPACE | 3 | 4"-129 | H | 3 m x 2.7 m + 4.2 m x 2.7 m | 209.2502 | 78 | 95 | 17 | 0.063 | ↔ | 224.107 |  | 224.107 | 70 | 70 | 0 |  |  | 0
STORE | 6 | 3"-94 | H | 1.2 m x 2.7 m + 0.8 m x 2.7 m | 34.875 | 78 | 78 | 0 | 0.158 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
DECK CHANGE ROOM | 6 | 3"-94 | H | 2.6 m x 2.7 m | 75.5626 | 78 | 78 | 0 | 0.158 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
PANTRY | 6 | 3"-94 | H | 5 m x 2.7 m | 145.3126 | 78 | 105 | 27 | 0.158 | ↔ | 619.9038 |  | 619.9038 | 70 | 70 | 0 |  |  | 0
ESCAPE TRUNK | 6 | 0"-6 | H | 0.8 m x 2.7 m | 23.25 | 78 | 120 | 42 | 0.313 | ↔ | 305.6448 |  | 305.6448 | 70 | 70 | 0 |  |  | 0
STAIRWAY | 6 | 3"-94 | H | 1.2 m x 2.7 m + 1.2 m x 2.7 m | 69.7501 | 78 | 80 | 2 | 0.158 | ↔ | 22.041 |  | 22.041 | 70 | 70 | 0 |  |  | 0
VENTILATION TRUNK | 6 | 0"-6 | H | 0.8 m x 2.7 m | 23.25 | 78 | 120 | 42 | 0.313 | ↔ | 305.6448 |  | 305.6448 | 70 | 70 | 0 |  |  | 0
ENGINE ROOM | 2 | 3"-94 | D |  | 261.778 | 78 | 130 | 52 | 0.144 | ↓ | 1960.194 |  | 1960.194 | 70 | 70 | 0 |  |  | 0
STAIRWAY | 2 | 3"-94 | D | 3 m x 1.2 m | 38.75 | 78 | 80 | 2 | 0.144 | ↓ | 11.16 |  | 11.16 | 70 | 70 | 0 |  |  | 0
CO2 ROOM | 1 | 3"-94 | U |  | 108.5001 | 78 | 110 | 32 | 0.171 | ↑ | 593.7126 |  | 593.7126 | 70 | 70 | 0 |  |  | 0
HOSPITAL | 1 | 3"-94 | U |  | 146.8196 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 6 | 3"-94 | H | 1 m x 2.7 m | 29.0625 | 78 | 80 | 2 | 0.158 | ↔ | 9.1838 |  | 9.1838 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 1 | 3"-94 | U | 0.6 m x 1 m | 6.4583 | 78 | 80 | 2 | 0.171 | ↑ | 2.2088 |  | 2.2088 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 4053.8006 | [5 empty] | 0
WINDOW |  |  |  |  | 12.9167 | [5 empty] | 2066.6688 |  | 2066.6688
LIGHTS | 7 |  |  |  | 300.5281 | [5 empty] | 1202.1124 |  | 1202.1124
EQUIPMENT: Convection Oven, Electric | 8 | [9 empty] | 13500 | 6900 | 20400
EQUIPMENT: Griddle, Electric | 8 | [9 empty] | 13500 | 6900 | 20400
EQUIPMENT: Mixer, Electric | 8 | [9 empty] | 1120 | 580 | 1700
EQUIPMENT: Refrigerator (up to 20 cu.ft.) | 8 | [9 empty] | 1300 |  | 1300
FOOD | 8 | [9 empty] | 630 | 630 | 1260
PERSONNEL | 9 | [9 empty] | 630 | 970 | 1600
TOTAL HEAT | [12 empty] | 53982.5817 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 53982.5817
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 300.5281 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 2662.1583 | cb. ft
|  |  |  | R of C | 88.7386 | CFM
|  |  |  | qS TOTAL | 38002.5817 | Btu/hr
|  |  |  | qL TOTAL | 15980 | Btu/hr
|  |  |  | qT TOTAL | 53982.5817 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 1407.503 | CFM
|  |  |  | CFM | 1408 | CFM
|  |  |  | Q (kW) | 0.41264 | kW
|  |  |  | SHF | 0.70398
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## CREW MESS
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
GALLEY |  | 5002 |  | POOP DECK | 16 ~ 24
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
OUTDOOR SPACE | 3 | 4"-129 | H | (5.8 m + 6 m) x 2.7 m | 342.9379 | 78 | 95 | 17 | 0.063 | ↔ | 367.2864 |  | 367.2864 | 70 | 70 | 0 |  |  | 0
PANTRY | 6 | 3"-94 | H | 4 m x 2.7 m | 116.2501 | 78 | 105 | 27 | 0.158 | ↔ | 495.923 |  | 495.923 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 6 | 3"-94 | H | (3 m + 3.5 m + 1.3 m) x 2.7 m | 226.6877 | 78 | 80 | 2 | 0.158 | ↔ | 71.6333 |  | 71.6333 | 70 | 70 | 0 |  |  | 0
ENGINE ROOM | 2 | 1"-22 | D |  | 298.16 | 78 | 130 | 52 | 0.199 | ↓ | 3085.36 |  | 3085.36 | 70 | 70 | 0 |  |  | 0
ENGINE WORKSHOP ROOM | 2 | 1"-22 | D | 5.8 m x 1.7 m | 106.1321 | 78 | 110 | 32 | 0.199 | ↓ | 675.8489 |  | 675.8489 | 70 | 70 | 0 |  |  | 0
AIR CONDITION ROOM | 1 | 3"-94 | U |  | 293.4239 | 78 | 110 | 32 | 0.171 | ↑ | 1605.6157 |  | 1605.6157 | 70 | 70 | 0 |  |  | 0
AB 1 CABIN | 1 | 3"-94 | U |  | 31.1077 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 1 | 3"-94 | U |  | 55.9723 | 78 | 80 | 2 | 0.171 | ↑ | 19.1425 |  | 19.1425 | 70 | 70 | 0 |  |  | 0
AB 1 TOILET | 1 | 3"-94 | U |  | 23.7882 | 78 | 85 | 7 | 0.171 | ↑ | 28.4745 |  | 28.4745 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 6349.2844 | [5 empty] | 0
WINDOW |  |  |  |  | 25.8334 | [5 empty] | 4133.3376 |  | 4133.3376
LIGHTS | 7 |  |  |  | 404.2921 | [5 empty] | 3234.3367 |  | 3234.3367
0
0
EQUIPMENT: Refrigerator (up to 20 cu.ft.) | 8 | [9 empty] | 1300 |  | 1300
FOOD | 8 | [9 empty] | 630 | 630 | 1260
PERSONNEL | 9 | [9 empty] | 3150 | 4850 | 8000
INFILTRATION
TOTAL HEAT | [12 empty] | 24276.9586 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 24276.9586
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 404.2921 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 3581.3276 | cb. ft
|  |  |  | R of C | 119.3776 | CFM
|  |  |  | qS TOTAL | 18796.9586 | Btu/hr
|  |  |  | qL TOTAL | 5480 | Btu/hr
|  |  |  | qT TOTAL | 24276.9586 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 696.1837 | CFM
|  |  |  | CFM | 697 | CFM
|  |  |  | Q (kW) | 0.20427 | kW
|  |  |  | SHF | 0.77427
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## OFFICE MESS
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
OFFICE MESS |  | 5003 |  | POOP DECK | 27 ~ 35
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
OUTDOOR SPACE | 3 | 4"-129 | H | (5.9 m + 6.4 m) x 2.7 m | 1097.4011 | 78 | 95 | 17 | 0.063 | ↔ | 1175.3166 |  | 1175.3166 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 6 | 3"-94 | H | (5.1 m + 1 m + 1.3 m) x 2.7 m | 215.0627 | 78 | 80 | 2 | 0.158 | ↔ | 67.9598 |  | 67.9598 | 70 | 70 | 0 |  |  | 0
SHIP OFFICE | 6 | 0"-6 | H | 4.9 m x 2.7 m | 142.4064 | 78 | 78 | 0 | 0.425 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
VALVE CONTROL UNIT ROOM | 2 | 1"-22 | D |  | 212.0488 | 78 | 110 | 32 | 0.199 | ↓ | 1350.3269 |  | 1350.3269 | 70 | 70 | 0 |  |  | 0
ENGINE CONTROL ROOM | 2 | 1"-25 | D |  | 182.8787 | 78 | 78 | 0 | 0.143 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
FITTER CABIN | 1 | 3"-94 | U |  | 144.7745 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
MESSMAN CABIN | 1 | 3"-94 | U |  | 134.2258 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 1 | 3"-94 | U |  | 54.8959 | 78 | 80 | 2 | 0.171 | ↑ | 18.7744 |  | 18.7744 | 70 | 70 | 0 |  |  | 0
FITTER TOILET | 1 | 3"-94 | U | 1.6 m x 1.7 m | 29.2778 | 78 | 85 | 7 | 0.171 | ↑ | 35.0455 |  | 35.0455 | 70 | 70 | 0 |  |  | 0
MESMAN TOILET | 1 | 3"-94 | U | 1.6 m x 1.7 m | 29.2778 | 78 | 85 | 7 | 0.171 | ↑ | 35.0455 |  | 35.0455 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 2682.4688 | [5 empty] | 0
WINDOW |  |  |  |  | 22.6042 | [5 empty] | 3616.6704 |  | 3616.6704
LIGHTS | 7 |  |  |  | 392.4518 | [5 empty] | 3139.6144 |  | 3139.6144
0
0
0
FOOD | 8 | [9 empty] | 300 | 300 | 600
PERSONNEL | 9 | [9 empty] | 3150 | 4850 | 8000
INFILTRATION
TOTAL HEAT | [12 empty] | 18038.7536 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 18038.7536
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 392.4518 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 3476.4432 | cb. ft
|  |  |  | R of C | 115.8814 | CFM
|  |  |  | qS TOTAL | 12888.7536 | Btu/hr
|  |  |  | qL TOTAL | 5150 | Btu/hr
|  |  |  | qT TOTAL | 18038.7536 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 477.3612 | CFM
|  |  |  | CFM | 478 | CFM
|  |  |  | Q (kW) | 0.14009 | kW
|  |  |  | SHF | 0.7145
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## SHIP OFFICE
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
SHIP OFFICE |  | 5004 |  | POOP DECK | 28 ~ 35
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
OUTDOOR SPACE | 3 | 4"-129 | H | 5.2 m x 2.7 m | 151.1252 | 78 | 95 | 17 | 0.073 | ↔ | 187.5463 |  | 187.5463 | 70 | 70 | 0 | 0.073 | ↔ | 0
PASSAGEWAY | 6 | 3"-94 | H | (1 m + 1.1 m + 1 m) x 2.7 m | 90.0938 | 78 | 80 | 2 | 0.158 | ↔ | 28.4697 |  | 28.4697 | 70 | 70 | 0 | 0.158 | ↔ | 0
STAIRWAY | 6 | 3"-94 | H | 3.1 m x 2.7 m | 90.0938 | 78 | 80 | 2 | 0.158 | ↔ | 28.4697 |  | 28.4697 | 70 | 70 | 0 | 0.158 | ↔ | 0
CARGO CONTROL ROOM | 6 | 3"-94 | H | 4.9 m x 2.7 m | 142.4064 | 78 | 78 | 0 | 0.158 | ↔ | 0 |  | 0 | 70 | 70 | 0 | 0.158 | ↔ | 0
OFFICE MESS | 6 | 0"-6 | H | 4.9 m x 2.7 m | 142.4064 | 78 | 78 | 0 | 0.425 | ↔ | 0 |  | 0 | 70 | 70 | 0 | 0.425 | ↔ | 0
ENGINE CONTROL ROOM | 2 | 1"-25 | D |  | 318.3962 | 78 | 78 | 0 | 0.161 | ↓ | 0 |  | 0 | 70 | 70 | 0 | 0.161 | ↓ | 0
MOTORMAN 1 CABIN | 1 | 3"-94 | U |  | 99.7814 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 | 0.171 | ↑ | 0
MOTORMAN 1 TOILET | 1 | 3"-94 | U | 0.6 m x 1.7 m | 10.9792 | 78 | 85 | 7 | 0.171 | ↑ | 13.1421 |  | 13.1421 | 70 | 70 | 0 | 0.171 | ↑ | 0
OS CABIN | 1 | 3"-94 | U |  | 134.2258 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 | 0.171 | ↑ | 0
PASSAGEWAY | 1 | 3"-94 | U |  | 44.132 | 78 | 80 | 2 | 0.171 | ↑ | 15.0931 |  | 15.0931 | 70 | 70 | 0 | 0.171 | ↑ | 0
OS TOILET | 1 | 3"-94 | U | 1.7 m x 1.6 m | 29.2778 | 78 | 85 | 7 | 0.171 | ↑ | 35.0455 |  | 35.0455 | 70 | 70 | 0 | 0.171 | ↑ | 0
TRANSMISSION SUBTOTAL | [12 empty] | 307.7664 | [5 empty] | 0
WINDOW |  |  |  |  | 12.9167 | [5 empty] | 2066.6688 |  | 2066.6688
LIGHTS | 7 |  |  |  | 318.3962 | [5 empty] | 2547.1693 |  | 2547.1693
EQUIPMENT: Computer | 8 | [9 empty] | 1842.48 |  | 1842.48
EQUIPMENT: Monitor LCD | 8 | [9 empty] | 491.328 |  | 491.328
EQUIPMENT: Printer | 8 | [9 empty] | 307.08 |  | 307.08
EQUIPMENT: Telephone | 8 | [9 empty] | 61.416 |  | 61.416
EQUIPMENT: Chart
PERSONNEL | 9 | [9 empty] | 630 | 970 | 1600
INFILTRATION
TOTAL HEAT | [12 empty] | 9223.9085 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 9223.9085
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 318.3962 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 2820.4385 | cb. ft
|  |  |  | R of C | 94.0146 | CFM
|  |  |  | qS TOTAL | 8253.9085 | Btu/hr
|  |  |  | qL TOTAL | 970 | Btu/hr
|  |  |  | qT TOTAL | 9223.9085 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 305.7003 | CFM
|  |  |  | CFM | 306 | CFM
|  |  |  | Q (kW) | 0.08968 | kW
|  |  |  | SHF | 0.89484
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## CARGO CONTROL ROOM
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
CARGO CONTROL ROOM |  | 5005 |  | POOP DECK | 28 ~ 35
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
OUTDOOR SPACE | 3 | 4"-129 | H | (4.2 m + 5.9 m) x 2.7 m | 293.5316 | 78 | 95 | 17 | 0.073 | ↔ | 364.2727 |  | 364.2727 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 6 | 3"-94 | H | (3.1 m + 1 m + 1.1 m) x 2.7 m | 151.1252 | 78 | 80 | 2 | 0.158 | ↔ | 47.7555 |  | 47.7555 | 70 | 70 | 0 |  |  | 0
SHIP OFFICE | 6 | 3"-94 | H | 4.9 m x 2.7 m | 142.4064 | 78 | 78 | 0 | 0.158 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
ENGINE CONTROL ROOM | 2 | 1"-25 | D |  | 165.9793 | 78 | 78 | 0 | 0.161 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
FIRE FOAM STATION | 2 | 1"-22 | D | 1.4 m x 5.9 m | 88.9098 | 78 | 110 | 32 | 0.199 | ↓ | 566.1777 |  | 566.1777 | 70 | 70 | 0 |  |  | 0
MOTORMAN 2 CABIN | 1 | 3"-94 | U |  | 139.5001 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
MOTORMAN 2 TOILET | 1 | 3"-94 | U |  | 26.0486 | 78 | 85 | 7 | 0.171 | ↑ | 31.1802 |  | 31.1802 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 1 | 3"-94 | U |  | 33.3681 | 78 | 80 | 2 | 0.171 | ↑ | 11.4119 |  | 11.4119 | 70 | 70 | 0 |  |  | 0
MOTORMAN 1 CABIN | 1 | 3"-94 | U | 3.2 m x 1 m | 34.4445 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
MOTORMAN 1 TOILET | 1 | 3"-94 | U | 1.7 m x 1 m | 18.2986 | 78 | 85 | 7 | 0.171 | ↑ | 21.9035 |  | 21.9035 | 70 | 70 | 0 |  |  | 0
MOTORMAN 2 TOILET VOID | 1 | 3"-94 | U |  | 3.2292 | 78 | 120 | 42 | 0.171 | ↑ | 23.1919 |  | 23.1919 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 1065.8934 | [5 empty] | 0
SOLAR |  |  |  |  | 12.9167 | [5 empty] | 2066.6688 |  | 2066.6688
LIGHTS | 7 |  |  |  | 254.8892 | [5 empty] | 2039.1132 |  | 2039.1132
EQUIPMENT: Cargo control console | 8
EQUIPMENT: Cargo pump control console | 8
EQUIPMENT: Computer | 8
EQUIPMENT: Electrical cabinet | 8
PERSONNEL | 9 | [9 empty] | 630 | 970 | 1600
INFILTRATION
TOTAL HEAT | [12 empty] | 6771.6754 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 6771.6754
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 254.8892 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 2257.8764 | cb. ft
|  |  |  | R of C | 75.2625 | CFM
|  |  |  | qS TOTAL | 5801.6754 | Btu/hr
|  |  |  | qL TOTAL | 970 | Btu/hr
|  |  |  | qT TOTAL | 6771.6754 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 214.8769 | CFM
|  |  |  | CFM | 215 | CFM
|  |  |  | Q (kW) | 0.06301 | kW
|  |  |  | SHF | 0.85676
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## DECK CHANGE ROOM
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
DECK CHANGE ROOM |  | 5006 |  | POOP DECK | 23 ~ 26
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 3"-94 | H | 2.6 m x 2.7 m | 81.3751 | 78 | 80 | 2 | 0.158 | ↔ | 25.7145 |  | 25.7145 | 70 | 70 | 0 |  |  | 0
STORE | 6 | 0"-6 | H | 2.4 m x 2.7 m | 63.9376 | 78 | 78 | 0 | 0.425 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
STAIRWAY | 6 | 3"-94 | H | 2.4 m x 2.7 m | 63.9376 | 78 | 80 | 2 | 0.158 | ↔ | 20.2043 |  | 20.2043 | 70 | 70 | 0 |  |  | 0
GALLEY | 6 | 3"-94 | H | 2.6 m x 2.7 m | 81.3751 | 78 | 78 | 0 | 0.158 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
ENGINE ROOM | 2 | 0"-0 | D | 2.6 m x 2.4 m | 51.4514 | 78 | 130 | 52 | 0.801 | ↓ | 2143.0555 |  | 2143.0555 | 70 | 70 | 0 |  |  | 0
AB 2 CABIN | 1 | 3"-94 | U |  | 60.3855 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
AB 2 TOILET | 1 | 3"-94 | U |  | 6.3938 | 78 | 85 | 7 | 0.171 | ↑ | 7.6533 |  | 7.6533 | 70 | 70 | 0 |  |  | 0
AB 2 TOILET VOID | 1 | 3"-94 | U |  | 0.3875 | 78 | 120 | 42 | 0.171 | ↑ | 2.783 |  | 2.783 | 70 | 70 | 0 |  |  | 0
HYDRAULIC OIL STORAGE TANK | 2 | 0"-0 | D |  | 15.7153 | 78 | 120 | 42 | 1.113 | ↑ | 734.6271 |  | 734.6271 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 2934.0377 | [5 empty] | 0
LIGHTS | 7 |  |  |  | 67.1667 | [5 empty] | 268.6669 |  | 268.6669
8
8
8
PERSONNEL | 9 | [9 empty] | 1260 | 1940 | 3200
INFILTRATION
TOTAL HEAT | [12 empty] | 6402.7047 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 6402.7047
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 67.1667 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 594.9809 | cb. ft
|  |  |  | R of C | 19.8327 | CFM
|  |  |  | qS TOTAL | 4462.7047 | Btu/hr
|  |  |  | qL TOTAL | 1940 | Btu/hr
|  |  |  | qT TOTAL | 6402.7047 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 165.2854 | CFM
|  |  |  | CFM | 166 | CFM
|  |  |  | Q (kW) | 0.04865 | kW
|  |  |  | SHF | 0.697
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## STORE
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
STORE |  | 5007 |  | POOP DECK | 23 ~ 26
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 3"-94 | H | (1.2 m + 1.7 m) x 2.7 m | 84.2813 | 78 | 80 | 2 | 0.158 | ↔ | 26.6329 |  | 26.6329 | 70 | 70 | 0 |  |  | 0
ENGINE ROOM | 2 | 0"-0 | D | 2.4 m x 1.2 m | 31 | 78 | 130 | 52 | 0.801 | ↓ | 1291.2133 |  | 1291.2133 | 70 | 70 | 0 |  |  | 0
AB 2 TOILET | 1 | 3"-94 | U |  | 20.4299 | 78 | 85 | 7 | 0.171 | ↑ | 24.4546 |  | 24.4546 | 70 | 70 | 0 |  |  | 0
AB 2 TOILET VOID | 1 | 3"-94 | U |  | 6.6941 | 78 | 120 | 42 | 1.171 | ↑ | 329.2277 |  | 329.2277 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 1671.5285 | [5 empty] | 0
LIGHTS | 7 |  |  |  | 31 | [5 empty] | 124.0001 |  | 124.0001
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 2595.5287 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 2595.5287
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 31 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 274.6066 | cb. ft
|  |  |  | R of C | 9.1536 | CFM
|  |  |  | qS TOTAL | 2110.5287 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 2595.5287 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 78.1677 | CFM
|  |  |  | CFM | 79 | CFM
|  |  |  | Q (kW) | 0.023153 | kW
|  |  |  | SHF | 0.81314
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## MOTORMAN 2 CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
MOTORMAN 2 CABIN |  | 6001 |  | A DECK | 28 ~ 35
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
MOTORMAN 2 TOILET | 6 | 0"-6 | H | (1.6 m + 0.9 m) x 2.7 m | 72.6563 | 78 | 85 | 7 | 0.425 | ↔ | 216.1526 |  | 216.1526 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 6 | 0"-6 | H | 1.6 m x 2.7 m | 46.5 | 78 | 80 | 2 | 0.425 | ↔ | 39.525 |  | 39.525 | 70 | 70 | 0 |  |  | 0
MOTORMAN 1 TOILET | 6 | 0"-6 | H | 1.7 m x 2.7 m | 49.4063 | 78 | 85 | 7 | 0.425 | ↔ | 146.9837 |  | 146.9837 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | (3 m + 2.7 m) x 2.7 m | 165.6564 | 78 | 95 | 17 | 0.073 | ↔ | 205.5796 |  | 205.5796 | 70 | 70 | 0 |  |  | 0
MOTORMAN 2 TOILET VOID | 6 | 0"-6 | H | 0.8 m x 2.7 m | 23.25 | 78 | 120 | 42 | 0.425 | ↔ | 415.0129 |  | 415.0129 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 1023.2539 | [5 empty] | 0
WINDOW |  |  |  |  | 6.4583 | [5 empty] | 1033.3344 |  | 1033.3344
LIGHTS | 7 |  |  |  | 139.5001 | [5 empty] | 558.0006 |  | 558.0006
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 3414.5889 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 3414.5889
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 139.5001 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1235.7297 | cb. ft
|  |  |  | R of C | 41.191 | CFM
|  |  |  | qS TOTAL | 2929.5889 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 3414.5889 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 108.5033 | CFM
|  |  |  | CFM | 109 | CFM
|  |  |  | Q (kW) | 0.031945 | kW
|  |  |  | SHF | 0.85796
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## MOTORMAN 1 CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
MOTORMAN 1 CABIN |  | 6002 |  | A DECK | 28 ~ 35
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
OUTDOOR SPACE | 6 | 0"-6 | SH | 3.1 m x 2.7 m | 90.0938 | 78 | 95 | 17 | 0.313 | ↔ | 479.3893 |  | 479.3893 | 70 | 70 | 0 |  |  | 0
MOTORMAN 1 TOILET | 6 | 0"-6 | SH | (1.6 m + 1.7 m) x 2.7 m | 95.9063 | 78 | 85 | 7 | 0.313 | ↔ | 210.1308 |  | 210.1308 | 70 | 70 | 0 |  |  | 0
OS TOILET | 6 | 0"-6 | SH | 1.7 m x 2.7 m | 49.4063 | 78 | 85 | 7 | 0.313 | ↔ | 108.2492 |  | 108.2492 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 2 | 3"-94 | SD | 1.5 m x 2.7 m | 43.5938 | 78 | 80 | 2 | 0.144 | ↓ | 12.555 |  | 12.555 | 70 | 70 | 0 |  |  | 0
2ND ENGINEER TOILET | 1 | 3"-94 | SU | 1.5 m x 2.1 m | 33.9063 | 78 | 85 | 7 | 0.171 | ↑ | 40.5858 |  | 40.5858 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 850.9102 | [5 empty] | 0
WINDOW |  |  |  |  | 6.4583 | [5 empty] | 1033.3344 |  | 1033.3344
LIGHTS | 7 |  |  |  | 134.2258 | [5 empty] | 536.9033 |  | 536.9033
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 3221.1479 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 3221.1479
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 134.2258 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1189.0084 | cb. ft
|  |  |  | R of C | 39.6336 | CFM
|  |  |  | qS TOTAL | 2736.1479 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 3221.1479 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 101.3388 | CFM
|  |  |  | CFM | 102 | CFM
|  |  |  | Q (kW) | 0.029893 | kW
|  |  |  | SHF | 0.84943
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## OS CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
OS CABIN |  | 6003 |  | A DECK | 28 ~ 35
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
OS TOILET | 6 | 0"-6 | H | (1.6 m + 1.7 m) x 2.7 m | 95.9063 | 78 | 85 | 7 | 0.313 | ↔ | 210.1308 |  | 210.1308 | 70 | 70 | 0 |  |  | 0
MESSMAN CABIN | 6 | 0"-6 | H | 4.9 m x 2.7 m | 142.4064 | 78 | 78 | 0 | 0.313 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
MOTORMAN 1 CABIN | 6 | 0"-6 | H | 3.2 m x 2.7 m | 93.0001 | 78 | 78 | 0 | 0.313 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 6 | 0"-6 | H | 1.5 m x 2.7 m | 43.5938 | 78 | 80 | 2 | 0.313 | ↔ | 27.2897 |  | 27.2897 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | 3.1 m x 2.7 m | 90.0938 | 78 | 95 | 17 | 0.063 | ↔ | 96.4905 |  | 96.4905 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 1 | 3"-94 | U | 0.3 m x 1.5 m | 4.8438 | 78 | 80 | 2 | 0.171 | ↑ | 1.6566 |  | 1.6566 | 70 | 70 | 0 |  |  | 0
OWNER ROOM CABIN | 1 | 3"-94 | U |  | 116.4654 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
SHIP OFFICE | 2 | 3"-94 | D |  | 134.2258 | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 335.5676 | [5 empty] | 0
WINDOW |  |  |  |  | 6.4583 | [5 empty] | 1033.3344 |  | 1033.3344
LIGHTS | 7 |  |  |  | 134.2258 | [5 empty] | 1073.8067 |  | 1073.8067
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 3242.7087 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 3242.7087
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 134.2258 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1189.0084 | cb. ft
|  |  |  | R of C | 39.6336 | CFM
|  |  |  | qS TOTAL | 2757.7087 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 3242.7087 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 102.1374 | CFM
|  |  |  | CFM | 103 | CFM
|  |  |  | Q (kW) | 0.030186 | kW
|  |  |  | SHF | 0.85043
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## AB 2 CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
AB 2 CABIN |  | 6004 |  | A DECK | 23 ~ 37
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
AB 2 TOILET | 6 | 0"-6 | H | (1.6 m + 1.7 m) x 2.7 m | 95.9063 | 78 | 85 | 7 | 0.313 | ↔ | 210.1308 |  | 210.1308 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 6 | 0"-6 | H | 4.9 m x 2.7 m | 142.4064 | 78 | 80 | 2 | 0.313 | ↔ | 89.1464 |  | 89.1464 | 70 | 70 | 0 |  |  | 0
HOSPITAL | 6 | 0"-6 | H | 3.2 m x 2.7 m | 93.0001 | 78 | 78 | 0 | 0.313 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 6 | 0"-6 | H | 1.5 m x 2.7 m | 43.5938 | 78 | 80 | 2 | 0.313 | ↔ | 27.2897 |  | 27.2897 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | 3.1 m x 2.7 m | 90.0938 | 78 | 95 | 17 | 0.063 | ↔ | 96.4905 |  | 96.4905 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 1 | 3"-94 | U | 0.1 m x 1.3 m | 1.3993 | 78 | 80 | 2 | 0.171 | ↑ | 0.47856 |  | 0.47856 | 70 | 70 | 0 |  |  | 0
3RD ENGINEER CABIN | 1 | 3"-94 | U |  | 116.4654 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
ELECTRICIAN CREW CABIN | 1 | 3"-94 | U |  | 134.2258 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
3RD ENGINEER TOILET | 1 | 3"-94 | U |  | 18.7292 | 78 | 85 | 7 | 0.171 | ↑ | 22.4188 |  | 22.4188 | 70 | 70 | 0 |  |  | 0
ELECTRICIAN CREW TOILET | 1 | 3"-94 | U |  | 3.0139 | 78 | 85 | 7 | 0.171 | ↑ | 3.6076 |  | 3.6076 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 2 | 3"-94 | D |  | 55.9723 | 78 | 80 | 2 | 0.144 | ↓ | 16.12 |  | 16.12 | 70 | 70 | 0 |  |  | 0
DECK CHANGE ROOM | 2 | 3"-94 | D |  | 60.3855 | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
STAIRWAY | 2 | 3"-94 | D |  | 36.1667 | 78 | 80 | 2 | 0.144 | ↓ | 10.416 |  | 10.416 | 70 | 70 | 0 |  |  | 0
STORE | 2 | 3"-94 | D |  | 3.875 | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 476.0985 | [5 empty] | 0
WINDOW |  |  |  |  | 3.2292 | [5 empty] | 516.6672 |  | 516.6672
LIGHTS | 7 |  |  |  | 156.3995 | [5 empty] | 625.5979 |  | 625.5979
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 2418.3636 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 2418.3636
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 156.3995 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1385.4284 | cb. ft
|  |  |  | R of C | 46.1809 | CFM
|  |  |  | qS TOTAL | 1933.3636 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 2418.3636 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 71.6061 | CFM
|  |  |  | CFM | 72 | CFM
|  |  |  | Q (kW) | 0.021101 | kW
|  |  |  | SHF | 0.79945
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## AB 1 CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
AB 1 CABIN |  | 6005 |  | A DECK | 23 ~ 37
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 0"-6 | H | (5 m + 1.4 m) x 2.7 m | 186.0002 | 78 | 80 | 2 | 0.313 | ↔ | 116.4361 |  | 116.4361 | 70 | 70 | 0 |  |  | 0
AIR COND ROOM | 6 | 3"-94 | H | 3.5 m x 2.7 m | 101.7189 | 78 | 110 | 32 | 0.158 | ↔ | 514.2905 |  | 514.2905 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | 3.5 m x 2.7 m | 101.7189 | 78 | 95 | 17 | 0.063 | ↔ | 108.9409 |  | 108.9409 | 70 | 70 | 0 |  |  | 0
AB 1 TOILET | 6 | 0"-6 | H | (1.5 m + 2.1) x 2.7 m | 104.6251 | 78 | 85 | 7 | 0.313 | ↔ | 229.2336 |  | 229.2336 | 70 | 70 | 0 |  |  | 0
3RD OFFICER CABIN | 1 | 3"-94 | U |  | 80.1911 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
3RD OFFICER TOILET | 1 | 3"-94 | U |  | 17.7604 | 78 | 85 | 7 | 0.171 | ↑ | 21.2592 |  | 21.2592 | 70 | 70 | 0 |  |  | 0
PUMPMAN CABIN | 1 | 3"-94 | U |  | 56.5105 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 2 | 3"-94 | D |  | 53.8195 | 78 | 80 | 2 | 0.144 | ↓ | 15.5 |  | 15.5 | 70 | 70 | 0 |  |  | 0
WC | 2 | 3"-94 | D |  | 30.6771 | 78 | 85 | 7 | 0.144 | ↓ | 30.9225 |  | 30.9225 | 70 | 70 | 0 |  |  | 0
CREW MESS | 2 | 3"-94 | D |  | 64.0452 | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
VOID | 2 | 3"-94 | D |  | 5.9201 | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 1036.5829 | [5 empty] | 0
WINDOW |  |  |  |  | 3.2292 | [5 empty] | 516.6672 |  | 516.6672
LIGHTS | 7 |  |  |  | 154.462 | [5 empty] | 617.8479 |  | 617.8479
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 2971.098 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 2971.098
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 154.462 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1368.2655 | cb. ft
|  |  |  | R of C | 45.6088 | CFM
|  |  |  | qS TOTAL | 2486.098 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 2971.098 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 92.0777 | CFM
|  |  |  | CFM | 93 | CFM
|  |  |  | Q (kW) | 0.027256 | kW
|  |  |  | SHF | 0.83676
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## FITTER CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
FITTER CABIN |  | 6006 |  | A DECK | 28 ~ 35
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 0"-6 | H | 1.7 m x 2.7 m | 49.4063 | 78 | 80 | 2 | 0.313 | ↔ | 30.9283 |  | 30.9283 | 70 | 70 | 0 |  |  | 0
MESSMAN CABIN | 6 | 0"-6 | H | 3.2 m x 2.7 m | 93.0001 | 78 | 78 | 0 | 0.313 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
FITTER TOILET | 6 | 0"-6 | H | (1.6 m + 1.7 m) x 2.7 m | 95.9063 | 78 | 85 | 7 | 0.313 | ↔ | 210.1308 |  | 210.1308 | 70 | 70 | 0 |  |  | 0
MESSMAN TOILET | 6 | 0"-6 | H | 1.7 m x 2.7 m | 49.4063 | 78 | 85 | 7 | 0.313 | ↔ | 108.2492 |  | 108.2492 | 70 | 70 | 0 |  |  | 0
2ND OFFICER CABIN | 1 | 3"-94 | U |  | 139.2849 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
3RD OFFICER CABIN | 1 | 3"-94 | U |  | 5.4896 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
OFFICE MESS | 2 | 3"-94 | D |  | 144.7745 | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | (3.2 m + 3.3 m) x 2.7 m | 188.9064 | 78 | 95 | 17 | 0.063 | ↔ | 202.3188 |  | 202.3188 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 551.6272 | [5 empty] | 0
WINDOW |  |  |  |  | 3.2292 | [5 empty] | 516.6672 |  | 516.6672
LIGHTS | 7 |  |  |  | 144.7745 | [5 empty] | 579.0978 |  | 579.0978
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 2447.3922 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 2447.3922
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 144.7745 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1282.4509 | cb. ft
|  |  |  | R of C | 42.7484 | CFM
|  |  |  | qS TOTAL | 1962.3922 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 2447.3922 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 72.6812 | CFM
|  |  |  | CFM | 73 | CFM
|  |  |  | Q (kW) | 0.021394 | kW
|  |  |  | SHF | 0.80183
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## MESSMAN CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
MESSMAN CABIN |  | 6007 |  | A DECK | 28 ~ 35
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 0"-6 | H | 1.5 m x 2.7 m | 43.5938 | 78 | 80 | 2 | 0.313 | ↔ | 27.2897 |  | 27.2897 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | 3.1 m x 2.7 m | 90.0938 | 78 | 95 | 17 | 0.063 | ↔ | 96.4905 |  | 96.4905 | 70 | 70 | 0 |  |  | 0
MESSMAN TOILET | 6 | 0"-6 | H | (1.6 m + 1.7 m) x 2.7 m | 95.9063 | 78 | 85 | 7 | 0.313 | ↔ | 210.1308 |  | 210.1308 | 70 | 70 | 0 |  |  | 0
FITTER CABIN | 6 | 0"-6 | H | 3.2 m x 2.7 m | 93.0001 | 78 | 78 | 0 | 0.313 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
OS CABIN | 6 | 0"-6 | H | 4.9 m x 2.7 m | 142.4064 | 78 | 78 | 0 | 0.313 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
2ND OFFICER CABIN | 1 | 3"-94 | U |  | 46.6077 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
2ND OFFICER TOILET | 1 | 3"-94 | U |  | 33.9063 | 78 | 85 | 7 | 0.171 | ↑ | 40.5858 |  | 40.5858 | 70 | 70 | 0 |  |  | 0
OWNER CABIN | 1 | 3"-94 | U |  | 27.8785 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
OWNER TOILET | 1 | 3"-94 | U |  | 20.9896 | 78 | 85 | 7 | 0.171 | ↑ | 25.1246 |  | 25.1246 | 70 | 70 | 0 |  |  | 0
3RD OFFICER CABIN | 1 | 3"-94 | U | (0.2 m + 0.3 m) x 2.7 m | 14.5313 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 1 | 3"-94 | U |  | 4.1979 | 78 | 85 | 7 | 0.171 | ↑ | 5.0249 |  | 5.0249 | 70 | 70 | 0 |  |  | 0
OFFICE MESS | 2 | 3"-94 | D |  | 134.2258 | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 404.6463 | [5 empty] | 0
SOLAR |  |  |  |  | 3.2292 | [5 empty] | 516.6672 |  | 516.6672
LIGHTS | 7 |  |  |  | 134.2258 | [5 empty] | 536.9033 |  | 536.9033
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 2258.2169 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 2258.2169
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 134.2258 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1189.0084 | cb. ft
|  |  |  | R of C | 39.6336 | CFM
|  |  |  | qS TOTAL | 1773.2169 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 2258.2169 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 65.6747 | CFM
|  |  |  | CFM | 66 | CFM
|  |  |  | Q (kW) | 0.019343 | kW
|  |  |  | SHF | 0.78523
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## SUEZ CREW
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
SUEZ CREW |  | 6008 |  | A DECK | 16 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 3"-94 | H | 5.6 m x 2.7 m | 162.7502 | 78 | 110 | 32 | 0.158 | ↔ | 822.8648 |  | 822.8648 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | 1.5 m x 2.7 m | 43.5938 | 78 | 95 | 17 | 0.073 | ↔ | 54.0999 |  | 54.0999 | 70 | 70 | 0 |  |  | 0
CO2 ROOM | 6 | 3"-94 | H | (1.6 m + 2.4 m) x 2.7 m | 116.2501 | 78 | 110 | 32 | 0.158 | ↔ | 587.7606 |  | 587.7606 | 70 | 70 | 0 |  |  | 0
STAIRWAY | 6 | 3"-94 | H | 2.1 m x 2.7 m | 61.0313 | 78 | 105 | 27 | 0.158 | ↔ | 260.3596 |  | 260.3596 | 70 | 70 | 0 |  |  | 0
VOID | 6 | 3"-94 | H | 1 m x 2.7 m | 29.0625 | 78 | 120 | 42 | 0.158 | ↔ | 192.8589 |  | 192.8589 | 70 | 70 | 0 |  |  | 0
HOSPITAL ROOM | 6 | 3"-94 | H | 1.7 m x 2.7 m | 49.4063 | 78 | 78 | 0 | 0.158 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
HOSPITAL TOILET | 6 | 3"-94 | H | 1.5 m x 2.7 m | 43.5938 | 78 | 110 | 32 | 0.158 | ↔ | 220.4102 |  | 220.4102 | 70 | 70 | 0 |  |  | 0
STORE (B DECK) | 1 | 3"-94 | U |  | 40.0417 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
BONDED STORE | 1 | 3"-94 | U |  | 65.4445 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
FAN ROOM | 1 | 3"-94 | U |  | 25.8334 | 78 | 110 | 32 | 0.171 | ↑ | 141.3601 |  | 141.3601 | 70 | 70 | 0 |  |  | 0
VOID | 1 | 3"-94 | U |  | 14.2083 | 78 | 120 | 42 | 0.171 | ↑ | 102.0444 |  | 102.0444 | 70 | 70 | 0 |  |  | 0
PANTRY | 2 | 3"-94 | D |  | 134.2258 | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 2381.7586 | [5 empty] | 0
SOLAR |  |  |  |  | 3.2292 | [5 empty] | 516.6672 |  | 516.6672
LIGHTS | 7 |  |  |  | 145.5279 | [5 empty] | 1164.2234 |  | 1164.2234
PERSONNEL | 9 | [9 empty] | 1890 | 2910 | 4800
INFILTRATION
TOTAL HEAT | [12 empty] | 8862.6492 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 8862.6492
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 145.5279 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1289.1254 | cb. ft
|  |  |  | R of C | 42.9708 | CFM
|  |  |  | qS TOTAL | 5952.6492 | Btu/hr
|  |  |  | qL TOTAL | 2910 | Btu/hr
|  |  |  | qT TOTAL | 8862.6492 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 220.4685 | CFM
|  |  |  | CFM | 221 | CFM
|  |  |  | Q (kW) | 0.064769 | kW
|  |  |  | SHF | 0.67166
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## HOSPITAL
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
HOSPITAL |  | 6009 |  | A DECK | 19 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 0"-6 | H | 1.1 m x 2.7 m | 31.9688 | 78 | 80 | 2 | 0.313 | ↔ | 20.0125 |  | 20.0125 | 70 | 70 | 0 |  |  | 0
AB 2 CABIN | 6 | 0"-6 | H | 1.5 m x 2.7 m | 43.5938 | 78 | 78 | 0 | 0.313 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
HOSPITAL TOILET | 6 | 0"-6 | H | (1.6 m + 2.4 m) x 2.7 m | 116.2501 | 78 | 78 | 0 | 0.313 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
CO2 ROOM | 6 | 3"-94 | H | 3.9 m x 2.7 m | 113.3439 | 78 | 110 | 32 | 0.158 | ↔ | 573.0666 |  | 573.0666 | 70 | 70 | 0 |  |  | 0
VOID | 6 | 3"-94 | H | 0.1 m x 2.7 m | 2.9063 | 78 | 120 | 42 | 0.158 | ↔ | 19.2859 |  | 19.2859 | 70 | 70 | 0 |  |  | 0
AB 2 TOILET | 6 | 0"-6 | H | 1.5 m x 2.7 m | 43.5938 | 78 | 85 | 7 | 0.313 | ↔ | 95.514 |  | 95.514 | 70 | 70 | 0 |  |  | 0
SUEZ CREW | 6 | 3"-94 | H | 1.7 m x 2.7 m | 49.4063 | 78 | 78 | 0 | 0.158 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
BOSUN CABIN | 1 | 3"-94 | U |  | 50.3751 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
ELECTRICIANMAN CABIN | 1 | 3"-94 | U |  | 106.2397 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
ELECTRICIANMAN TOILET | 1 | 3"-94 | U |  | 5.1667 | 78 | 85 | 7 | 0.171 | ↑ | 6.1845 |  | 6.1845 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 1 | 3"-94 | U |  | 23.25 | 78 | 80 | 2 | 0.171 | ↑ | 7.9515 |  | 7.9515 | 70 | 70 | 0 |  |  | 0
GALLEY | 2 | 3"-94 | D |  | 163.9342 | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
STAIRWAY | 2 | 3"-94 | D |  | 21.0972 | 78 | 80 | 2 | 0.144 | ↓ | 6.076 |  | 6.076 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | 3.3 m x 2.7 m | 95.9063 | 78 | 95 | 17 | 0.073 | ↔ | 119.0198 |  | 119.0198 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 847.1107 | [5 empty] | 0
SOLAR |  |  |  |  | 3.2292 | [5 empty] | 516.6672 |  | 516.6672
LIGHTS | 7 |  |  |  | 185.0314 | [5 empty] | 1480.2515 |  | 1480.2515
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 3644.0295 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 3644.0295
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 185.0314 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1639.0581 | cb. ft
|  |  |  | R of C | 54.6353 | CFM
|  |  |  | qS TOTAL | 3159.0295 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 3644.0295 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 117.0011 | CFM
|  |  |  | CFM | 118 | CFM
|  |  |  | Q (kW) | 0.034582 | kW
|  |  |  | SHF | 0.86691
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## HOSPITAL TOILET
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
HOSPITAL TOILET |  | 6010 |  | A DECK | 19 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
HOSPITAL | 6 | 0"-6 | H |  |  | 78 | 78 | 0 | 0.313 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
SUEZ CREW ROOM | 6 | 3"-94 | H |  |  | 78 | 78 | 0 | 0.158 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
CO2 ROOM | 6 | 3"-94 | H | 2.4 m x 2.7 m | 69.7501 | 78 | 110 | 32 | 0.158 | ↔ | 352.6564 |  | 352.6564 | 70 | 70 | 0 |  |  | 0
ELECTRICIANMAN CABIN | 1 | 3"-94 | U |  |  | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
BOSUN CABIN | 1 | 3"-94 | U | 0.1 m x 2.7 m |  | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
PASAGEWAY | 1 | 3"-94 | U |  | 18.2986 | 78 | 80 | 2 | 0.171 | ↑ | 6.2581 |  | 6.2581 | 70 | 70 | 0 |  |  | 0
GALLEY | 2 | 3"-94 | D |  |  | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 358.9145 | [5 empty] | 0
SOLAR |  |  |  |  | 3.2292 | [5 empty] | 516.6672 |  | 516.6672
LIGHTS | 7 |  |  |  | 38.75 | [5 empty] | 310.0003 |  | 310.0003
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 1985.582 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 1985.582
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 38.75 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 343.2582 | cb. ft
|  |  |  | R of C | 11.4419 | CFM
|  |  |  | qS TOTAL | 1500.582 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 1985.582 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 55.5771 | CFM
|  |  |  | CFM | 56 | CFM
|  |  |  | Q (kW) | 0.016412 | kW
|  |  |  | SHF | 0.75574
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## GYM ROOM
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
GYM |  | 7001 |  | B DECK | 19 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
OUTDOOR SPACE | 3 | 3"-94 | H | 2.4 m x 2.7 m | 69.7501 | 78 | 95 | 17 | 0.158 | ↔ | 187.3487 |  | 187.3487 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 3"-94 | H | 2.4 m x 2.7 m | 69.7501 | 78 | 95 | 17 | 0.158 | ↔ | 187.3487 |  | 187.3487 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 3"-94 | H | 2.4 m x 2.7 m | 69.7501 | 78 | 95 | 17 | 0.158 | ↔ | 187.3487 |  | 187.3487 | 70 | 70 | 0 |  |  | 0
FAN ROOM | 6 | 3"-94 | H | 2.8 m x 2.7 m | 81.3751 | 78 | 110 | 32 | 0.158 | ↔ | 411.4324 |  | 411.4324 | 70 | 70 | 0 |  |  | 0
VOID | 6 | 3"-94 | H | 0.4 m x 2.7 m | 11.625 | 78 | 120 | 42 | 0.158 | ↔ | 77.1436 |  | 77.1436 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 1 | 3"-94 | U | 2.4 m x 3.2 m | 82.6668 | 78 | 95 | 17 | 0.171 | ↑ | 240.3122 |  | 240.3122 | 70 | 70 | 0 |  |  | 0
OUTDOOR SAPCE | 2 | 3"-94 | D | 2.4 m x 3.2 m | 82.6668 | 78 | 95 | 17 | 0.144 | ↓ | 202.3682 |  | 202.3682 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 1493.3025 | [5 empty] | 0
WINDOW |  |  |  |  | 3.2292 | [5 empty] | 516.6672 |  | 516.6672
LIGHTS | 7 |  |  |  | 889.8167 | [5 empty] | 3559.2666 |  | 3559.2666
PERSONNEL | 9 | [9 empty] | 945 | 1455 | 2400
INFILTRATION
TOTAL HEAT | [12 empty] | 7969.2363 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 7969.2363
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 889.8167 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 7882.2344 | cb. ft
|  |  |  | R of C | 262.7411 | CFM
|  |  |  | qS TOTAL | 6514.2363 | Btu/hr
|  |  |  | qL TOTAL | 1455 | Btu/hr
|  |  |  | qT TOTAL | 7969.2363 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 241.268 | CFM
|  |  |  | CFM | 242 | CFM
|  |  |  | Q (kW) | 0.070923 | kW
|  |  |  | SHF | 0.81742
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## BOSUN CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
BOSUN CABIN |  | 7002 |  | B DECK | 19 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 0"-6 | H | 1.9 m x 2.7 m | 55.2188 | 78 | 80 | 2 | 0.313 | ↔ | 34.567 |  | 34.567 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | 3.6 m x 2.7 m | 104.6251 | 78 | 95 | 17 | 0.158 | ↔ | 281.023 |  | 281.023 | 70 | 70 | 0 |  |  | 0
ELECTRICIANMAN CABIN | 6 | 0"-6 | H | 5.1 m x 2.7 m | 148.2189 | 78 | 78 | 0 | 0.313 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | 3.5 m x 2.7 m | 101.7189 | 78 | 95 | 17 | 0.171 | ↔ | 295.6967 |  | 295.6967 | 70 | 70 | 0 |  |  | 0
BOSUN TOILET | 3 | 0"-6 | H | (1.6 m + 1.7 m) x 2.7 m | 95.9063 | 78 | 85 | 7 | 0.313 | ↔ | 210.1308 |  | 210.1308 | 70 | 70 | 0 |  |  | 0
PILOT CABIN | 1 | 3"-94 | U |  | 139.3925 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
PILOT TOILET | 1 | 3"-94 | U |  | 6.9965 | 78 | 85 | 7 | 0.144 | ↑ | 7.0525 |  | 7.0525 | 70 | 70 | 0 |  |  | 0
CHIEF OFFICER BEDROOM | 1 | 3"-94 | U |  |  | 78 | 78 | 0 | 0.144 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
CHIEF OFFICER TOILET | 1 | 3"-94 | U |  | 5.5972 | 78 | 85 | 7 | 0.144 | ↑ | 5.642 |  | 5.642 | 70 | 70 | 0 |  |  | 0
HOSPITAL | 2 | 3"-94 | D |  |  | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
HOSPITAL TOILET | 2 | 3"-94 | D |  |  | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
CO2 ROOM | 2 | 3"-94 | D |  | 102.4723 | 78 | 110 | 32 | 0.144 | ↓ | 472.1925 |  | 472.1925 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 1306.3045 | [5 empty] | 0
WINDOW |  |  |  |  | 3.2292 | [5 empty] | 516.6672 |  | 516.6672
LIGHTS | 7 |  |  |  | 168.3474 | [5 empty] | 1346.7792 |  | 1346.7792
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 3969.7509 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 3969.7509
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 168.3474 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1491.2664 | cb. ft
|  |  |  | R of C | 49.7089 | CFM
|  |  |  | qS TOTAL | 3484.7509 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 3969.7509 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 129.0648 | CFM
|  |  |  | CFM | 130 | CFM
|  |  |  | Q (kW) | 0.038099 | kW
|  |  |  | SHF | 0.87783
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## ELECTRICIANMAN CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
ELECTRICIANMAN CABIN |  | 7003 |  | B DECK | 19 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGE WAY | 6 | 0"-6 | H | 1.8 m x 2.7 m | 52.3126 | 78 | 80 | 2 | 0.313 | ↔ | 32.7477 |  | 32.7477 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | 3.6 m x 2.7 m | 104.6251 | 78 | 95 | 17 | 0.063 | ↔ | 112.0535 |  | 112.0535 | 70 | 70 | 0 |  |  | 0
ELECTRICIANMAN TOILET | 6 | 0"-6 | H | (1.6 m + 1.7 m) x 2.7 m | 95.9063 | 78 | 85 | 7 | 0.313 | ↔ | 210.1308 |  | 210.1308 | 70 | 70 | 0 |  |  | 0
CHIEF OFFICER TOILET | 1 | 3"-94 | U |  | 25.1875 | 78 | 85 | 7 | 0.171 | ↑ | 30.1495 |  | 30.1495 | 70 | 70 | 0 |  |  | 0
HOSPITAL TOILET | 2 | 3"-94 | D |  | 3.875 | 78 | 85 | 7 | 0.144 | ↓ | 3.906 |  | 3.906 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 388.9874 | [5 empty] | 0
WINDOW |  |  |  |  | 6.4583 | [5 empty] | 1033.3344 |  | 1033.3344
LIGHTS | 7 |  |  |  | 38.75 | [5 empty] | 310.0003 |  | 310.0003
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 2532.3222 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 2532.3222
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 38.75 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 343.2582 | cb. ft
|  |  |  | R of C | 11.4419 | CFM
|  |  |  | qS TOTAL | 2047.3222 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 2532.3222 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 75.8267 | CFM
|  |  |  | CFM | 76 | CFM
|  |  |  | Q (kW) | 0.022273 | kW
|  |  |  | SHF | 0.80848
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## 3RD ENGINEER CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
3RD ENGINEER CABIN |  | 7004 |  | B DECK | 25 ~ 30
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 0"-6 | H | 1.8 m x 2.7 m | 52.3126 | 78 | 80 | 2 | 0.313 | ↔ | 32.7477 |  | 32.7477 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | 3.5 m x 2.7 m | 101.7189 | 78 | 95 | 17 | 0.073 | ↔ | 126.2331 |  | 126.2331 | 70 | 70 | 0 |  |  | 0
3RD ENGINEER TOILET | 6 | 0"-6 | H | (1.7 + 1.6) m x 2.7 m | 95.9063 | 78 | 85 | 7 | 0.313 | ↔ | 210.1308 |  | 210.1308 | 70 | 70 | 0 |  |  | 0
MASTER TOILET | 1 | 3"-94 | U |  | 19.6441 | 78 | 85 | 7 | 0.171 | ↑ | 23.514 |  | 23.514 | 70 | 70 | 0 |  |  | 0
MASTER TOILET VOID | 1 | 3"-94 | U |  | 1.3455 | 78 | 120 | 42 | 0.171 | ↑ | 9.6633 |  | 9.6633 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 2 | 3"-94 | D | 1.2 m x 5.1 m | 65.8751 | 78 | 80 | 2 | 0.144 | ↓ | 18.972 |  | 18.972 | 70 | 70 | 0 |  |  | 0
MOTORMAN 2 TOILET | 2 | 3"-94 | D |  | 3.283 | 78 | 85 | 7 | 0.144 | ↓ | 3.3093 |  | 3.3093 | 70 | 70 | 0 |  |  | 0
MOTORMAN 2 TOILET VOID | 2 | 3"-94 | D |  | 1.8837 | 78 | 120 | 42 | 0.144 | ↓ | 11.3925 |  | 11.3925 | 70 | 70 | 0 |  |  | 0
MOTORMAN 1 TOILET | 2 | 3"-94 | D |  | 3.283 | 78 | 85 | 7 | 0.144 | ↓ | 3.3093 |  | 3.3093 | 70 | 70 | 0 |  |  | 0
MOTORMAN 1 TOILET VOID | 2 | 3"-94 | D |  | 1.8837 | 78 | 120 | 42 | 0.144 | ↓ | 11.3925 |  | 11.3925 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 450.6644 | [5 empty] | 0
WINDOW |  |  |  |  | 6.4583 | [5 empty] | 1033.3344 |  | 1033.3344
LIGHTS | 7 |  |  |  | 162.8578 | [5 empty] | 651.4312 |  | 651.4312
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 2935.43 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 2935.43
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 162.8578 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1442.6381 | cb. ft
|  |  |  | R of C | 48.0879 | CFM
|  |  |  | qS TOTAL | 2450.43 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 2935.43 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 90.7567 | CFM
|  |  |  | CFM | 91 | CFM
|  |  |  | Q (kW) | 0.026669 | kW
|  |  |  | SHF | 0.83478
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## 2ND ENGINEER CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
2ND ENGINEER CABIN |  | 7005 |  | B DECK | 19 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
2ND ENGINEER TOILET | 6 | 0"-6 | H | (1.5 m + 2.1 m) x 2.7 m | 104.6251 | 78 | 85 | 7 | 0.313 | ↔ | 229.2336 |  | 229.2336 | 70 | 70 | 0 |  |  | 0
MOTORMAN 2 TOILET | 2 | 3"-94 | D |  | 22.7656 | 78 | 85 | 7 | 0.144 | ↓ | 22.9478 |  | 22.9478 | 70 | 70 | 0 |  |  | 0
MOTORMAN 2 TOILET VOID | 2 | 3"-94 | D |  | 1.3455 | 78 | 120 | 42 | 0.144 | ↓ | 8.1375 |  | 8.1375 | 70 | 70 | 0 |  |  | 0
MOTORMAN 1 TOILET | 2 | 3"-94 | D |  | 22.7656 | 78 | 85 | 7 | 0.144 | ↓ | 22.9478 |  | 22.9478 | 70 | 70 | 0 |  |  | 0
MOTORMAN 1 TOILET VOID | 2 | 3"-94 | D |  | 1.3455 | 78 | 120 | 42 | 0.144 | ↓ | 8.1375 |  | 8.1375 | 70 | 70 | 0 |  |  | 0
OS TOILET | 2 | 3"-94 | D | 0.2 m x 1.1 m | 2.3681 | 78 | 85 | 7 | 0.144 | ↓ | 2.387 |  | 2.387 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | (3.8 m x 4.6 m) x 2.7 m | 244.1253 | 78 | 95 | 17 | 0.063 | ↔ | 261.4581 |  | 261.4581 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 6 | 0"-6 | H | 1.4 m x 2.7 m | 40.6875 | 78 | 80 | 2 | 0.313 | ↔ | 25.4704 |  | 25.4704 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 580.7197 | [5 empty] | 0
WINDOW |  |  |  |  | 9.6875 | [5 empty] | 1550.0016 |  | 1550.0016
LIGHTS | 7 |  |  |  | 242.7259 | [5 empty] | 1213.6297 |  | 1213.6297
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 4144.351 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 4144.351
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 242.7259 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 2150.1315 | cb. ft
|  |  |  | R of C | 71.671 | CFM
|  |  |  | qS TOTAL | 3659.351 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 4144.351 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 135.5315 | CFM
|  |  |  | CFM | 136 | CFM
|  |  |  | Q (kW) | 0.039858 | kW
|  |  |  | SHF | 0.88297
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## OWNER CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
OWNER CABIN |  | 7009 |  | B DECK | 19 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 0"-6 | H | 3 m x 2.7 m | 87.1876 | 78 | 80 | 2 | 0.313 | ↔ | 54.5794 |  | 54.5794 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | 5.4 m x 2.7 m | 156.9377 | 78 | 95 | 17 | 0.063 | ↔ | 168.0802 |  | 168.0802 | 70 | 70 | 0 |  |  | 0
OWNER TOIILET | 6 | 0"-6 | H | (0.9 m + 1.5 m + 2.1 m) x 2.7 m | 130.7814 | 78 | 85 | 7 | 0.313 | ↔ | 286.542 |  | 286.542 | 70 | 70 | 0 |  |  | 0
2ND OFFICER TOILET | 6 | 0"-6 | H | 1.1 m x 2.7 m | 31.9688 | 78 | 85 | 7 | 0.313 | ↔ | 70.0436 |  | 70.0436 | 70 | 70 | 0 |  |  | 0
2ND OFFICER TOILET VOID | 6 | 0"-6 | H | 0.8 m x 2.7 m | 23.25 | 78 | 120 | 42 | 0.313 | ↔ | 305.6448 |  | 305.6448 | 70 | 70 | 0 |  |  | 0
2ND ENGINEER TOILET | 6 | 0"-6 | H | 1.3 m x 2.7 m | 37.7813 | 78 | 85 | 7 | 0.313 | ↔ | 82.7788 |  | 82.7788 | 70 | 70 | 0 |  |  | 0
2ND ENGINEER TOILET VOID | 6 | 0"-6 | H | 0.8 m x 2.7 m | 23.25 | 78 | 120 | 42 | 0.313 | ↔ | 305.6448 |  | 305.6448 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 1 | 3"-94 | U |  | 8.2882 | 78 | 80 | 2 | 0.171 | ↑ | 2.8346 |  | 2.8346 | 70 | 70 | 0 |  |  | 0
OS TOILET | 2 | 3"-94 | D |  | 20.3976 | 78 | 85 | 7 | 0.144 | ↓ | 20.5608 |  | 20.5608 | 70 | 70 | 0 |  |  | 0
OS TOILET VOID | 2 | 3"-94 | D |  | 1.3455 | 78 | 120 | 42 | 0.144 | ↓ | 8.1375 |  | 8.1375 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 1304.8466 | [5 empty] | 0
WINDOW |  |  |  |  | 12.9167 | [5 empty] | 2066.6688 |  | 2066.6688
LIGHTS | 7 |  |  |  | 203.7606 | [5 empty] | 815.0425 |  | 815.0425
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 4986.5579 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 4986.5579
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 203.7606 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1804.9662 | cb. ft
|  |  |  | R of C | 60.1655 | CFM
|  |  |  | qS TOTAL | 4501.5579 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 4986.5579 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 166.7244 | CFM
|  |  |  | CFM | 167 | CFM
|  |  |  | Q (kW) | 0.048943 | kW
|  |  |  | SHF | 0.90274
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## BONDED STATION
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
BONDED STORE |  | 7006 |  | B DECK | 18 ~ 22
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
VOID | 6 | 0"-6 | H | 2.4 m x 2.7 m | 69.7501 | 78 | 120 | 42 | 0.313 | ↔ | 916.9344 |  | 916.9344 | 70 | 70 | 0 | 0.313 | ↔ | 0
FAN ROOM | 6 | 0"-0 | H | 2.8 m x 2.7 m | 81.3751 | 78 | 110 | 32 | 0.93 | ↔ | 2421.7225 |  | 2421.7225 | 70 | 70 | 0 | 0.93 | ↔ | 0
PASSAGEWAY | 6 | 3"-94 | H | 2.4 m x 2.7 m | 69.7501 | 78 | 80 | 2 | 0.158 | ↔ | 22.041 |  | 22.041 | 70 | 70 | 0 | 0.158 | ↔ | 0
BATTERY ROOM | 1 | 3"-94 | U | 1.2 m x 1.2 m | 15.5 | 78 | 110 | 32 | 0.171 | ↑ | 84.8161 |  | 84.8161 | 70 | 70 | 0 | 0.171 | ↑ | 0
CO2 ROOM | 2 | 3"-94 | U | 0.4 m x 1.6 m | 6.8889 | 78 | 110 | 32 | 0.144 | ↓ | 31.744 |  | 31.744 | 70 | 70 | 0 | 0.144 | ↓ | 0
TRANSMISSION SUBTOTAL | [12 empty] | 3477.2581 | [5 empty] | 0
WINDOW |  |  |  |  | 0 | [5 empty] | 0 |  | 0
LIGHTS | 7 |  |  |  | 72.3334 | [5 empty] | 289.3336 |  | 289.3336
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 4566.5917 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 4566.5917
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 72.3334 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 640.7487 | cb. ft
|  |  |  | R of C | 21.3583 | CFM
|  |  |  | qS TOTAL | 4081.5917 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 4566.5917 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 151.1701 | CFM
|  |  |  | CFM | 152 | CFM
|  |  |  | Q (kW) | 0.044547 | kW
|  |  |  | SHF | 0.89379
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## STORE B DECK
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
STORE |  | 7007 |  | B DECK | 21 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
STAIRWAY | 6 | 0"-6 | H | 2.1 m x 2.7 m | 61.0313 | 78 | 80 | 2 | 0.313 | ↔ | 38.2056 |  | 38.2056 | 70 | 70 | 0 |  |  | 0
VOID TRUNK | 6 | 0"-0 | H | 1 m x 2.7 m | 29.0625 | 78 | 120 | 42 | 0.93 | ↔ | 1135.1824 |  | 1135.1824 | 70 | 70 | 0 |  |  | 0
VOID | 6 | 0"-6 | H | (1.2 m + 0.3 m) x 2.7 m | 43.5938 | 78 | 120 | 42 | 0.313 | ↔ | 573.084 |  | 573.084 | 70 | 70 | 0 |  |  | 0
BONDED STORE | 6 | 0"-0 | H | 2.8 m x 2.7 m | 81.3751 | 78 | 78 | 0 | 1.113 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 6 | 3"-94 | H | 1.2 m x 2.7 m | 34.875 | 78 | 80 | 2 | 0.171 | ↑ | 11.9273 |  | 11.9273 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 1758.3993 | [5 empty] | 0
WINDOW |  |  |  |  | 0 | [5 empty] | 0 |  | 0
LIGHTS | 7 |  |  |  | 40.0417 | [5 empty] | 160.1668 |  | 160.1668
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 2718.5661 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 2718.5661
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 40.0417 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 354.7002 | cb. ft
|  |  |  | R of C | 11.8233 | CFM
|  |  |  | qS TOTAL | 2233.5661 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 2718.5661 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 82.7247 | CFM
|  |  |  | CFM | 83 | CFM
|  |  |  | Q (kW) | 0.024325 | kW
|  |  |  | SHF | 0.8216
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## 2ND OFFICER CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
2ND OFFICER CABIN |  | 7008 |  | B DECK | 29 ~ 35
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 0"-6 | H | 1.2 m x 2.7 m | 34.875 | 78 | 80 | 2 | 0.313 | ↔ | 21.8318 |  | 21.8318 | 70 | 70 | 0 |  |  | 0
2ND OFFICER TOILET | 6 | 0"-6 | H | (2.1 m + 1.5 m) x 2.7 m | 104.6251 | 78 | 85 | 7 | 0.313 | ↔ | 229.2336 |  | 229.2336 | 70 | 70 | 0 |  |  | 0
OWNER ROOM TOILET VOID TRUNK | 6 | 0"-6 | H | (0.8 m + 0.6 m) x 2.7 m | 40.6875 | 78 | 120 | 42 | 0.313 | ↔ | 534.8784 |  | 534.8784 | 70 | 70 | 0 |  |  | 0
OWNER ROOM TOILET | 6 | 0"-6 | H | (0.5 m + 0.6 m) x 2.7 m | 31.9688 | 78 | 85 | 7 | 0.313 | ↔ | 70.0436 |  | 70.0436 | 70 | 70 | 0 |  |  | 0
FITTER TOILET | 2 | 3"-94 | D |  | 22.7656 | 78 | 85 | 7 | 0.171 | ↓ | 27.2505 |  | 27.2505 | 70 | 70 | 0 |  |  | 0
MESSMAN TOILET | 2 | 3"-94 | D |  | 18.2986 | 78 | 85 | 7 | 0.171 | ↓ | 21.9035 |  | 21.9035 | 70 | 70 | 0 |  |  | 0
FITTER TOILET VOID TRUNK | 2 | 3"-94 | D |  | 22.7656 | 78 | 120 | 42 | 0.144 | ↓ | 137.6866 |  | 137.6866 | 70 | 70 | 0 |  |  | 0
MESSMAN TOILET VOID TRUNK | 2 | 3"-94 | D |  | 18.2986 | 78 | 120 | 42 | 1.144 | ↓ | 879.2126 |  | 879.2126 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 1922.0406 | [5 empty] | 0
WINDOW |  |  |  |  | 9.6875 | [5 empty] | 1550.0016 |  | 1550.0016
LIGHTS | 7 |  |  |  | 234.1148 | [5 empty] | 936.4593 |  | 936.4593
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 5208.5015 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 5208.5015
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 234.1148 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 2073.8519 | cb. ft
|  |  |  | R of C | 69.1284 | CFM
|  |  |  | qS TOTAL | 4723.5015 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 5208.5015 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 174.9445 | CFM
|  |  |  | CFM | 175 | CFM
|  |  |  | Q (kW) | 0.051287 | kW
|  |  |  | SHF | 0.90688
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## 3RD OFFICER CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
3RD OFFICER CABIN |  | 7009 |  | B DECK | 25 ~ 29
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 0"-6 | H | 1.8 m x 2.7 m | 52.3126 | 78 | 80 | 2 | 0.313 | ↔ | 32.7477 |  | 32.7477 | 70 | 70 | 0 |  |  | 0
3RD OFFICER TOILET | 6 | 0"-6 | H | (1.6 m + 1.7 m) x 2.7 m | 95.9063 | 78 | 85 | 7 | 0.313 | ↔ | 210.1308 |  | 210.1308 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 2 | 3"-94 | D |  | 66.198 | 78 | 80 | 2 | 0.144 | ↓ | 19.065 |  | 19.065 | 70 | 70 | 0 |  |  | 0
FITTER TOILET | 2 | 3"-94 | D |  | 3.283 | 78 | 85 | 7 | 0.144 | ↓ | 3.3093 |  | 3.3093 | 70 | 70 | 0 |  |  | 0
FITTER TOILET VOID TRUNK | 2 | 3"-94 | D |  | 1.8837 | 78 | 120 | 42 | 0.144 | ↓ | 11.3925 |  | 11.3925 | 70 | 70 | 0 |  |  | 0
MESSMAN TOILET | 2 | 3"-94 | D |  | 3.283 | 78 | 85 | 7 | 0.144 | ↓ | 3.3093 |  | 3.3093 | 70 | 70 | 0 |  |  | 0
MESSMAN TOILET VOID TRUNK | 2 | 3"-94 | D |  | 1.8837 | 78 | 120 | 42 | 0.144 | ↓ | 11.3925 |  | 11.3925 | 70 | 70 | 0 |  |  | 0
CHIEF ENGINEER TOILET | 1 | 3"-94 | U |  | 19.6441 | 78 | 85 | 7 | 0.171 | ↑ | 23.514 |  | 23.514 | 70 | 70 | 0 |  |  | 0
CHIEF ENGINEER TOILET VOID TRUNK | 1 | 3"-94 | U |  | 1.3455 | 78 | 120 | 42 | 0.171 | ↑ | 9.6633 |  | 9.6633 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | 3.5 m x 2.7 m | 101.7189 | 78 | 95 | 17 | 0.073 | ↔ | 126.2331 |  | 126.2331 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 450.7574 | [5 empty] | 0
WINDOW |  |  |  |  | 6.4583 | [5 empty] | 1033.3344 |  | 1033.3344
LIGHTS | 7 |  |  |  | 162.8578 | [5 empty] | 651.4312 |  | 651.4312
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 2935.523 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 2935.523
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 162.8578 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1442.6381 | cb. ft
|  |  |  | R of C | 48.0879 | CFM
|  |  |  | qS TOTAL | 2450.523 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 2935.523 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 90.7601 | CFM
|  |  |  | CFM | 91 | CFM
|  |  |  | Q (kW) | 0.026669 | kW
|  |  |  | SHF | 0.83478
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## PUMPMAN CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
PUMPMAN CABIN |  | 7010 |  | B DECK | 19 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 0"-6 | H | 1.8 m x 2.7 m | 52.3126 | 78 | 80 | 2 | 0.313 | ↔ | 32.7477 |  | 32.7477 | 70 | 70 | 0 |  |  | 0
3RD OFFICER TOILET | 6 | 0"-6 | H | (1.6 m + 1.7 m) x 2.7 m | 95.9063 | 78 | 85 | 7 | 0.313 | ↔ | 210.1308 |  | 210.1308 | 70 | 70 | 0 |  |  | 0
AIR CONDITIONAIR ROOM | 2 | 3"-94 | D |  | 104.4098 | 78 | 110 | 32 | 0.144 | ↓ | 481.1205 |  | 481.1205 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 2 | 3"-94 | D |  | 1.9375 | 78 | 80 | 2 | 0.144 | ↓ | 0.558 |  | 0.558 | 70 | 70 | 0 |  |  | 0
1ST ENGINEER TOILET | 1 | 3"-94 | U |  | 21.9584 | 78 | 85 | 7 | 0.171 | ↑ | 26.2842 |  | 26.2842 | 70 | 70 | 0 |  |  | 0
1ST ENGINEER TOILET VOID TRUNK | 1 | 3"-94 | U |  | 3.2292 | 78 | 120 | 42 | 0.171 | ↑ | 157.7049 |  | 157.7049 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | 3.5 m x 2.7 m | 101.7189 | 78 | 95 | 17 | 0.073 | ↔ | 4.0074 |  | 4.0074 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 912.5534 | [5 empty] | 0
WINDOW |  |  |  |  | 6.4583 | [5 empty] | 1033.3344 |  | 1033.3344
LIGHTS | 7 |  |  |  | 162.8578 | [5 empty] | 651.4312 |  | 651.4312
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 3397.3191 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 3397.3191
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 162.8578 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1442.6381 | cb. ft
|  |  |  | R of C | 48.0879 | CFM
|  |  |  | qS TOTAL | 2912.3191 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 3397.3191 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 107.8637 | CFM
|  |  |  | CFM | 108 | CFM
|  |  |  | Q (kW) | 0.031652 | kW
|  |  |  | SHF | 0.85724
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## COOKMAN CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
COOKMAN CABIN |  | 7011 |  | B DECK | 19 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 0"-6 | H | 1.8 m x 2.7 m | 52.3126 | 78 | 80 | 2 | 0.313 | ↔ | 32.7477 |  | 32.7477 | 70 | 70 | 0 |  |  | 0
COOKMAN TOILET TOILET | 6 | 0"-6 | H | (1.6 m + 1.7 m) x 2.7 m | 95.9063 | 78 | 85 | 7 | 0.313 | ↔ | 210.1308 |  | 210.1308 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 6 | 4"-129 | H | (3.5 m + 3.6 m) x 2.7 m | 206.344 | 78 | 95 | 17 | 0.073 | ↔ | 256.0729 |  | 256.0729 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 1 | 3"-94 | U |  | 146.389 | 78 | 95 | 17 | 0.171 | ↑ | 425.5529 |  | 425.5529 | 70 | 70 | 0 |  |  | 0
1ST ENGINEER TOILET | 1 | 3"-94 | U |  | 2.2604 | 78 | 80 | 2 | 0.171 | ↑ | 0.77306 |  | 0.77306 | 70 | 70 | 0 |  |  | 0
1ST ENGINEER TOILET VOID TRUNK | 1 | 3"-94 | U |  | 3.3368 | 78 | 120 | 42 | 0.171 | ↑ | 23.965 |  | 23.965 | 70 | 70 | 0 |  |  | 0
AIR CONDITIONAIR ROOM | 2 | 3"-94 | D |  | 166.3023 | 78 | 110 | 32 | 0.144 | ↓ | 766.3208 |  | 766.3208 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 2 | 3"-94 | D |  | 2.0451 | 78 | 80 | 2 | 0.144 | ↓ | 0.589 |  | 0.589 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 1716.1521 | [5 empty] | 0
WINDOW |  |  |  |  | 6.4583 | [5 empty] | 1033.3344 |  | 1033.3344
LIGHTS | 7 |  |  |  | 168.3474 | [5 empty] | 673.3896 |  | 673.3896
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 4222.8761 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 4222.8761
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 168.3474 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1491.2664 | cb. ft
|  |  |  | R of C | 49.7089 | CFM
|  |  |  | qS TOTAL | 3737.8761 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 4222.8761 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 138.4399 | CFM
|  |  |  | CFM | 139 | CFM
|  |  |  | Q (kW) | 0.040737 | kW
|  |  |  | SHF | 0.88515
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## PILOT CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
PILOT CABIN |  | 8001 |  | C DECK | 16 ~ 20
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 0"-6 | H | 1 m x 2.7 m | 29.0625 | 78 | 80 | 2 | 0.313 | ↔ | 18.1931 |  | 18.1931 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | (3.2 m + 3.8 m) x 2.7 m | 203.4377 | 78 | 95 | 17 | 0.073 | ↔ | 252.4662 |  | 252.4662 | 70 | 70 | 0 |  |  | 0
CHIEF OFFICER TOILET VOID TRUNK | 6 | 0"-6 | H | 1.4 m x 2.7 m | 40.6875 | 78 | 120 | 42 | 0.313 | ↔ | 534.8784 |  | 534.8784 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 1 | 3"-94 | U |  | 145.9585 | 78 | 95 | 17 | 0.171 | ↑ | 424.3013 |  | 424.3013 | 70 | 70 | 0 |  |  | 0
BOSUN TOILET | 2 | 3"-94 | D |  | 5.4896 | 78 | 85 | 7 | 0.144 | ↓ | 5.5335 |  | 5.5335 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 2 | 3"-94 | D |  | 1.0764 | 78 | 80 | 2 | 0.144 | ↓ | 0.31 |  | 0.31 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 1235.6826 | [5 empty] | 0
WINDOW |  |  |  |  | 3.2292 | [5 empty] | 516.6672 |  | 516.6672
LIGHTS | 7 |  |  |  | 145.9585 | [5 empty] | 583.8339 |  | 583.8339
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 3136.1837 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 3136.1837
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 145.9585 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1292.9394 | cb. ft
|  |  |  | R of C | 43.098 | CFM
|  |  |  | qS TOTAL | 2651.1837 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 3136.1837 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 98.192 | CFM
|  |  |  | CFM | 99 | CFM
|  |  |  | Q (kW) | 0.029014 | kW
|  |  |  | SHF | 0.84535
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## CHIEF OFFICER CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
CHIEF OFFICER CABIN |  | 1001 |  | C DECK | 19 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 0"-6 | H | 2.7 m x 2.7 m | 78.4688 | 78 | 80 | 2 | 0.313 | ↔ | 49.1215 |  | 49.1215 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | 3.8 m x 2.7 m | 110.4376 | 78 | 95 | 17 | 0.073 | ↔ | 137.0531 |  | 137.0531 | 70 | 70 | 0 |  |  | 0
MASTER TOILET | 6 | 0"-6 | H | 1 m x 2.7 m | 29.0625 | 78 | 85 | 7 | 0.313 | ↔ | 63.676 |  | 63.676 | 70 | 70 | 0 |  |  | 0
MASTER TOILET VOID TRUNK | 6 | 0"-6 | H | (1.4 m + 0.1 m) x 2.7 m | 43.5938 | 78 | 120 | 42 | 0.313 | ↔ | 573.084 |  | 573.084 | 70 | 70 | 0 |  |  | 0
CHIEF OFFICER TOILET | 6 | 0"-6 | H | 1.3 m x 2.7 m | 37.7813 | 78 | 85 | 7 | 0.313 | ↔ | 82.7788 |  | 82.7788 | 70 | 70 | 0 |  |  | 0
CHIEF OFFICER TOILET VOID TRUNK | 6 | 0"-6 | H | 0.1 m x 2.7 m | 2.9063 | 78 | 120 | 42 | 0.313 | ↔ | 38.2056 |  | 38.2056 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 1 | 3"-94 | U |  | 113.7292 | 78 | 95 | 17 | 0.171 | ↑ | 330.6108 |  | 330.6108 | 70 | 70 | 0 |  |  | 0
WHEEL HOUSE | 3 | 3"-94 | U |  |  | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
ELECTRICIANMAN TOILET | 2 | 3"-94 | D |  | 26.0486 | 78 | 85 | 7 | 0.144 | ↓ | 26.257 |  | 26.257 | 70 | 70 | 0 |  |  | 0
ELECTRICIANMAN TOILET VOID TRUNK | 2 | 3"-94 | D |  | 3.2292 | 78 | 120 | 42 | 0.144 | ↓ | 19.53 |  | 19.53 | 70 | 70 | 0 |  |  | 0
3RD ENGINEER TOILET | 2 | 3"-94 | D |  | 16.2535 | 78 | 85 | 7 | 0.144 | ↓ | 16.3835 |  | 16.3835 | 70 | 70 | 0 |  |  | 0
3RD ENGINEER TOILET VOID TRUNK | 2 | 3"-94 | D |  | 3.2292 | 78 | 120 | 42 | 0.144 | ↓ | 19.53 |  | 19.53 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 2 | 3"-94 | D |  | 2.9063 | 78 | 80 | 2 | 0.144 | ↓ | 0.837 |  | 0.837 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 1357.0674 | [5 empty] | 0
WINDOW |  |  |  |  | 6.4583 | [5 empty] | 1033.3344 |  | 1033.3344
LIGHTS | 7 |  |  |  | 196.1183 | [5 empty] | 784.473 |  | 784.473
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 3974.8748 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 3974.8748
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 196.1183 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1737.2681 | cb. ft
|  |  |  | R of C | 57.9089 | CFM
|  |  |  | qS TOTAL | 3489.8748 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 3974.8748 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 129.2546 | CFM
|  |  |  | CFM | 130 | CFM
|  |  |  | Q (kW) | 0.038099 | kW
|  |  |  | SHF | 0.87798
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## CHIEF OFFICER BEDROOM
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
CHIEF OFFICER BEDROOM |  | 1001 |  | C DECK | 19 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
OUTDOOR SPACE | 3 | 4"-129 | H | 2.2 m x 2.7 m | 63.9376 | 78 | 95 | 17 | 0.073 | ↔ | 79.3465 |  | 79.3465 | 70 | 70 | 0 |  |  | 0
CHIEF OFFICER TOILET | 6 | 0"-6 | H | 2.1 m x 2.7 m | 61.0313 | 78 | 85 | 7 | 0.313 | ↔ | 133.7196 |  | 133.7196 | 70 | 70 | 0 |  |  | 0
CHIEF OFFICER TOILET VOID TRUNK | 6 | 0"-6 | H | 0.1 m x 2.7 m | 2.9063 | 78 | 120 | 42 | 0.313 | ↔ | 38.2056 |  | 38.2056 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 1 | 3"-94 | U |  | 89.9862 | 78 | 95 | 17 | 0.171 | ↑ | 261.5899 |  | 261.5899 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 512.8616 | [5 empty] | 0
WINDOW |  |  |  |  | 3.2292 | [5 empty] | 516.6672 |  | 516.6672
LIGHTS | 7 |  |  |  | 89.9862 | [5 empty] | 359.9448 |  | 359.9448
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 2189.4736 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 2189.4736
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 89.9862 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 797.1219 | cb. ft
|  |  |  | R of C | 26.5707 | CFM
|  |  |  | qS TOTAL | 1704.4736 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 2189.4736 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 63.1287 | CFM
|  |  |  | CFM | 64 | CFM
|  |  |  | Q (kW) | 0.018757 | kW
|  |  |  | SHF | 0.77849
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## MASTER CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
MASTER CABIN |  | 1001 |  | C DECK | 19 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
PASSAGEWAY | 6 | 0"-6 | H | 1.2 m x 2.7 m | 34.875 | 78 | 78 | 0 | 0.425 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
MASTER TOILET | 6 | 0"-6 | H | 1.3 m x 2.7 m | 69.7501 | 78 | 78 | 0 | 0.158 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
MASTER TOILET VOID TRUNK | 6 | 0"-6 | H | 0.1 m x 2.7 m | 2.9063 | 78 | 110 | 32 | 0.158 | ↔ | 14.694 |  | 14.694 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | (3.8 m + 4.25 m) x 2.7 m | 233.9534 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 1 | 3"-94 | U |  | 69.2022 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
2ND ENGINEER TOILET | 2 | 3"-94 | D |  | 10.1719 | 78 | 110 | 32 | 0.171 | ↑ | 55.6606 |  | 55.6606 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 2 | 3"-94 | D |  | 4.1979 | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 70.3546 | [5 empty] | 0
WINDOW |  |  |  |  | 9.6875 | [5 empty] | 1550.0016 |  | 1550.0016
LIGHTS | 7 |  |  |  | 206.8822 | [5 empty] | 1241.2929 |  | 1241.2929
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 3661.6491 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 3661.6491
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 206.8822 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1832.6176 | cb. ft
|  |  |  | R of C | 61.0873 | CFM
|  |  |  | qS TOTAL | 3176.6491 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 3661.6491 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 117.6537 | CFM
|  |  |  | CFM | 118 | CFM
|  |  |  | Q (kW) | 0.034582 | kW
|  |  |  | SHF | 0.86755
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## MASTER BEDROOM
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
MASTER BEDROOM |  | 1001 |  | C DECK | 27 ~ 30
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
OUTDOOR SPACE | 6 | 4"-129 | H | 2.2 m x 2.7 m | 63.9376 | 78 | 95 | 17 | 0.073 | ↔ | 79.3465 |  | 79.3465 | 70 | 70 | 0 |  |  | 0
MASTER TOILET | 6 | 0"-6 | H | 1.1 m x 2.7 m | 31.9688 | 78 | 85 | 7 | 0.313 | ↔ | 70.0436 |  | 70.0436 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 1 | 3"-94 | U |  | 0.61247 | 78 | 95 | 17 | 0.171 | ↑ | 1.7804 |  | 1.7804 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 151.1706 | [5 empty] | 0
WINDOW |  |  |  |  | 3.2292 | [5 empty] | 516.6672 |  | 516.6672
LIGHTS | 7 |  |  |  | 86.7301 | [5 empty] | 346.9205 |  | 346.9205
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 1814.7583 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 1814.7583
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 86.7301 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 768.2787 | cb. ft
|  |  |  | R of C | 25.6093 | CFM
|  |  |  | qS TOTAL | 1329.7583 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 1814.7583 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 49.2503 | CFM
|  |  |  | CFM | 50 | CFM
|  |  |  | Q (kW) | 0.014654 | kW
|  |  |  | SHF | 0.73275
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## OFFICE
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
OFFICE |  | 1001 |  | C DECK | 29 ~ 35
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
OUTDOOR SPACE | 3 | 4"-129 | H | 7.3 m x 2.7 m | 212.1565 | 78 | 95 | 17 | 0.073 | ↔ | 263.2862 |  | 263.2862 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 6 | 0"-6 | H | (1 m + 1.9 m + 1.1 m) x 2.7 m | 116.2501 | 78 | 80 | 2 | 0.313 | ↔ | 72.7726 |  | 72.7726 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 3"-94 | U |  | 62.8612 | 78 | 95 | 17 | 0.171 | ↑ | 182.7374 |  | 182.7374 | 70 | 70 | 0 |  |  | 0
OWNER TOILET | 2 | 3"-94 | D |  | 33.9063 | 78 | 85 | 7 | 0.144 | ↓ | 34.1775 |  | 34.1775 | 70 | 70 | 0 |  |  | 0
2ND OFFICER TOILET | 2 | 3"-94 | D |  | 19.2136 | 78 | 80 | 2 | 0.144 | ↓ | 5.5335 |  | 5.5335 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 2 | 3"-94 | D |  | 6.1354 | 78 | 80 | 2 | 0.144 | ↓ | 1.767 |  | 1.767 | 70 | 70 | 0 |  |  | 0
2ND ENGINEER TOILET | 2 | 3"-94 | D |  | 23.7344 | 78 | 85 | 7 | 0.144 | ↓ | 23.9243 |  | 23.9243 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 584.1985 | [5 empty] | 0
WINDOW |  |  |  |  | 12.9167 | [5 empty] | 2066.6688 |  | 2066.6688
LIGHTS | 7 |  |  |  | 324.2625 | [5 empty] | 1297.0499 |  | 1297.0499
PERSONNEL | 9 | [9 empty] | 2520 | 3880 | 6400
INFILTRATION
TOTAL HEAT | [12 empty] | 10347.9173 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 10347.9173
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 324.2625 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 2872.404 | cb. ft
|  |  |  | R of C | 95.7468 | CFM
|  |  |  | qS TOTAL | 6467.9173 | Btu/hr
|  |  |  | qL TOTAL | 3880 | Btu/hr
|  |  |  | qT TOTAL | 10347.9173 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 239.5525 | CFM
|  |  |  | CFM | 240 | CFM
|  |  |  | Q (kW) | 0.070337 | kW
|  |  |  | SHF | 0.62505
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## INSTRUMENTATION ROOM
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
INTRUMENTATION ROOM |  | 1001 |  | C DECK | 18 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
STAIRWAY | 6 | 3"-94 | H |  | 61.0313 | 78 | 80 | 2 | 0.158 | ↔ | 19.2859 |  | 19.2859 | 70 | 70 | 0 |  |  | 0
VOID | 6 | 3"-94 | H |  | 29.0625 | 78 | 120 | 42 | 0.158 | ↔ | 192.8589 |  | 192.8589 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 6 | 3"-94 | H |  | 186.0002 | 78 | 80 | 2 | 0.158 | ↔ | 58.7761 |  | 58.7761 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H |  | 46.5 | 78 | 95 | 17 | 0.063 | ↔ | 49.8016 |  | 49.8016 | 70 | 70 | 0 |  |  | 0
BATTERY ROOM | 6 | 3"-94 | H |  | 90.0938 | 78 | 110 | 32 | 0.158 | ↔ | 455.5145 |  | 455.5145 | 70 | 70 | 0 |  |  | 0
STORE B DECK | 2 | 3"-94 | D |  | 90.0938 | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
BONDED STORE | 2 | 3"-94 | D |  | 40.0417 | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
FAN ROOM | 2 | 3"-94 | D |  | 6.8889 | 78 | 110 | 32 | 0.144 | ↓ | 31.744 |  | 31.744 | 70 | 70 | 0 |  |  | 0
VOID | 2 | 3"-94 | D |  | 3.875 | 78 | 120 | 42 | 0.144 | ↓ | 23.436 |  | 23.436 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 3"-94 | U |  | 79.5097 | 78 | 95 | 17 | 0.171 | ↑ | 231.1347 |  | 231.1347 | 70 | 70 | 0 |  |  | 0
WHEEL HOUSE | 1 | 3"-94 | U |  | 0 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
VOID | 1 | 3"-94 | U |  | 23.5622 | 78 | 120 | 42 | 0.171 | ↑ | 169.2236 |  | 169.2236 | 70 | 70 | 0 |  |  | 0
WC | 1 | 3"-94 | U | 0.343 m x 1 m | 3.692 | 78 | 85 | 7 | 0.171 | ↑ | 4.4193 |  | 4.4193 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 1236.1946 | [5 empty] | 0
WINDOW |  |  |  |  | 0 | [5 empty] | 0 |  | 0
LIGHTS | 7 |  |  |  | 107.639 | [5 empty] | 430.556 |  | 430.556
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 2466.7506 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 2466.7506
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 107.639 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 953.4951 | cb. ft
|  |  |  | R of C | 31.7832 | CFM
|  |  |  | qS TOTAL | 1981.7506 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 2466.7506 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 73.3982 | CFM
|  |  |  | CFM | 74 | CFM
|  |  |  | Q (kW) | 0.021687 | kW
|  |  |  | SHF | 0.80339
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## 1ST ENGINEER CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
1ST ENGINEER CABIN |  | 1001 |  | C DECK | 29 ~ 35
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
CHIEF ENGINEER TOILET | 6 | 0"-6 | H | 1.4 m x 2.7 m | 40.6875 | 78 | 85 | 7 | 0.313 | ↔ | 89.1464 |  | 89.1464 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 6 | 0"-6 | H | 2.7 m x 2.7 m | 78.4688 | 78 | 80 | 2 | 0.313 | ↔ | 49.1215 |  | 49.1215 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | 3.8 m x 2.7 m | 110.4376 | 78 | 95 | 17 | 0.063 | ↔ | 118.2787 |  | 118.2787 | 70 | 70 | 0 |  |  | 0
1ST ENGINEER TOILET | 6 | 0"-6 | H | 1.4 m x 2.7 m | 40.6875 | 78 | 85 | 7 | 0.313 | ↔ | 89.1464 |  | 89.1464 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 3"-94 | U |  | 113.7314 | 78 | 95 | 17 | 0.171 | ↑ | 330.6171 |  | 330.6171 | 70 | 70 | 0 |  |  | 0
WHEEL HOUSE | 1 | 3"-94 | U |  | 82.3869 | 78 | 78 | 0 | 0.171 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
PUMPMAN TOILET | 2 | 3"-94 | D |  | 29.2778 | 78 | 85 | 7 | 0.144 | ↓ | 29.512 |  | 29.512 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 2 | 3"-94 | D |  | 2.9063 | 78 | 80 | 2 | 0.144 | ↓ | 0.837 |  | 0.837 | 70 | 70 | 0 |  |  | 0
3RD OFFICER TOILET | 2 | 3"-94 | D |  | 19.4827 | 78 | 85 | 7 | 0.144 | ↓ | 19.6385 |  | 19.6385 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 726.2976 | [5 empty] | 0
WINDOW |  |  |  |  | 6.4583 | [5 empty] | 1033.3344 |  | 1033.3344
LIGHTS | 7 |  |  |  | 196.1183 | [5 empty] | 784.473 |  | 784.473
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 3344.1051 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 3344.1051
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 196.1183 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1737.2681 | cb. ft
|  |  |  | R of C | 57.9089 | CFM
|  |  |  | qS TOTAL | 2859.1051 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 3344.1051 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 105.8928 | CFM
|  |  |  | CFM | 106 | CFM
|  |  |  | Q (kW) | 0.031066 | kW
|  |  |  | SHF | 0.85497
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## 1ST ENGINEER BEDROOM
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
1ST ENGINEER BEDROOM |  | 1001 |  | C DECK | 20 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | ΔT | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
1ST ENGINEER TOILET | 6 | 0"-6 | H | 2.2 m x 2.7 m | 63.9376 | 78 | 85 | 7 | 0.313 | ↔ | 140.0872 |  | 140.0872 | 70 | 70 | 0 |  |  | 0
1ST ENGINEER CABIN | 6 | 0"-6 | H |  |  | 78 | 78 | 0 | 0.313 | ↔ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 4"-129 | H | (3.8 m + 2.2 m) x 2.7 m | 174.3752 | 78 | 95 | 17 | 0.063 | ↔ | 186.7558 |  | 186.7558 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 3 | 3"-94 | U | 3.8 m x 2.2 m | 89.9862 | 78 | 95 | 17 | 0.171 | ↑ | 261.5899 |  | 261.5899 | 70 | 70 | 0 |  |  | 0
PUMPMAN CABIN | 2 | 3"-94 | D |  |  | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
COOKMAN CABIN | 2 | 3"-94 | D |  |  | 78 | 78 | 0 | 0.144 | ↓ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 588.4329 | [5 empty] | 0
WINDOW |  |  |  |  | 6.4583 | [5 empty] | 1033.3344 |  | 1033.3344
LIGHTS | 7 |  |  |  | 89.9862 | [5 empty] | 359.9448 |  | 359.9448
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [12 empty] | 2781.7121 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 2781.7121
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 89.9862 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 797.1219 | cb. ft
|  |  |  | R of C | 26.5707 | CFM
|  |  |  | qS TOTAL | 2296.7121 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 2781.7121 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 85.0634 | CFM
|  |  |  | CFM | 86 | CFM
|  |  |  | Q (kW) | 0.025204 | kW
|  |  |  | SHF | 0.82565
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | ΔT = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## CHIEF ENGINEER CABIN
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
CHIEF ENGINEER CABIN |  | 1001 |  | C DECK | 29 ~ 35
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | Td | U |  | qS | qL | qT | T | T0 | ΔT | U |  | qW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
OUTDOOR SPACE | 3 | 4"-129 | H | (3.8 m + 4.25 m) x 2.7 m | 233.9534 | 78 | 95 | 17 | 0.073 | ↔ | 290.3361 |  | 290.3361 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 6 | 0"-6 | H | (1.2 m + 1 m) x 2.7 m | 63.9376 | 78 | 80 | 2 | 0.313 | ↔ | 40.0249 |  | 40.0249 | 70 | 70 | 0 |  |  | 0
CHIEF ENGINEER TOILET | 6 | 0"-6 | H | 1.4 m x 2.7 m | 40.6875 | 78 | 85 | 7 | 0.313 | ↔ | 89.1464 |  | 89.1464 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 1 | 3"-94 | D |  | 69.2011 | 78 | 95 | 17 | 0.171 | ↓ | 201.1676 |  | 201.1676 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 2 | 3"-94 | U |  | 4.1979 | 78 | 80 | 2 | 0.171 | ↑ | 1.4357 |  | 1.4357 | 70 | 70 | 0 |  |  | 0
2ND OFFICER TOILET | 2 | 3"-94 | U |  | 14.6927 | 78 | 85 | 7 | 0.171 | ↑ | 17.5872 |  | 17.5872 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 639.698 | [5 empty] | 0
WINDOW |  |  |  |  | 9.6875 | [5 empty] | 1550.0016 |  | 1550.0016
LIGHTS | 7 |  |  |  | 206.8822 | [5 empty] | 827.5286 |  | 827.5286
LIGHTS | 7 |  |  |  | 206.8822 | [5 empty] | 61.416 | [8 empty] | 2883 | 20
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL HEAT | [10 empty] | 3393.6442 | 485 | 3817.2282 | [5 empty] | 0
TOTAL HEAT | [5 empty] | 3817.2282
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 206.8822 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 1832.6176 | cb. ft
|  |  |  | R of C | 61.0873 | CFM
|  |  |  | qS TOTAL | 3393.6442 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 3817.2282 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 125.6905 | CFM
|  |  |  | CFM | 126 | CFM
|  |  |  | Q (kW) | 0.036927 | kW
|  |  |  | SHF | 0.88903
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | T = Space Design Temp. | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | TO = Temperature of | [°F] | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Adjacent Space / Outside |  | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] | Td = Temperature Difference | [°F] | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## CHIEF ENGINEER BEDROOM
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
CHIEF ENGINEER BEDROOM |  | 1001 |  | C DECK | 27 ~ 30
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | Td | U |  | qS | qL | qT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
CHIEF ENGINEER TOILET | 6 | 0"-6 | H | 1.1 m x 2.7 m | 31.9688 | 78 | 85 | 7 | 0.313 | ↔ | 70.0436 |  | 70.0436 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 6 | 4"-129 | H | 2.2 m x 2.7 m | 63.9376 | 78 | 95 | 17 | 0.063 | ↔ | 68.4771 |  | 68.4771 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 6 | 3"-94 | D |  | 0.61354 | 78 | 95 | 17 | 0.171 | ↓ | 1.7836 |  | 1.7836 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 140.3043 | [5 empty] | 0
WINDOW |  |  |  |  | 9.6875 | [5 empty] | 1550.0016 |  | 1550.0016
LIGHTS | 7 |  |  |  | 86.7301 | [5 empty] | 346.9205 |  | 346.9205
PERSONNEL | 9 | [9 empty] | 315 | 485 | 800
INFILTRATION
TOTAL | [10 empty] | 2352.2264 | 485 | 2837.2264 | [5 empty] | 0
TOTAL | [5 empty] | 2837.2264
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 86.7301 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 768.2787 | cb. ft
|  |  |  | R of C | 25.6093 | CFM
|  |  |  | qS TOTAL | 2352.2264 | Btu/hr
|  |  |  | qL TOTAL | 485 | Btu/hr
|  |  |  | qT TOTAL | 2837.2264 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 87.1195 | CFM
|  |  |  | CFM | 88 | CFM
|  |  |  | Q (kW) | 0.02579 | kW
|  |  |  | SHF | 0.82906
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | TO = Temperature of | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | Adjacent Space / Outside |  | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Td = Temperature Difference | [°F] | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] |  |  | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## WHEEL HOUSE
SPACE |  | SPACE NO. |  | DECK | FRAMES | SPACE TEMP COOLING 78 °F | [7 empty] | SPACE TEMP HEATING 70 °F
WHEEL HOUSE |  | 1001 |  | BRIDGE DECK | 19 ~ 23
ADJOINING SPACE | LOAD KEY | INSUL TYPE | U KEY | DIMENSION | AREA [ft2] | T | T0 | Td | U |  | QS | QL | QT | T | T0 | ΔT | U |  | QW
[9 empty] | COEFF | DIR | [6 empty] | COEFF | DIR
OUTDOOR SPACE | 3 | 4"-129 | H | (2.8 m + 7.6 m + 8.0718/2 m + 7.8/2 m + 4.8 m + 5 m) x 2.9 m | 1756.5417 | 78 | 95 | 17 | 0.073 | ↔ | 2179.8682 |  | 2179.8682 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE PORTSIDE | 2 | 3"-94 | U |  | 68.1247 | 78 | 95 | 17 | 0.144 | ↑ | 166.7693 |  | 166.7693 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE STARBOARD SIDE | 2 | 3"-94 | U |  | 68.1247 | 78 | 95 | 17 | 0.144 | ↑ | 166.7693 |  | 166.7693 | 70 | 70 | 0 |  |  | 0
MASTER CABIN | 2 | 3"-94 | U |  |  | 78 | 78 | 0 | 0.144 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
MASTER TOILET | 2 | 3"-94 | U |  | 33.1528 | 78 | 85 | 7 | 0.144 | ↑ | 33.418 |  | 33.418 | 70 | 70 | 0 |  |  | 0
CHIEF OFFICER TOILET | 2 | 3"-94 | U |  |  | 78 | 85 | 7 | 0.144 | ↑ | 0 |  | 0 | 70 | 70 | 0 |  |  | 0
PASSAGEWAY | 2 | 3"-94 | U |  | 196.4304 | 78 | 80 | 2 | 0.144 | ↑ | 56.572 |  | 56.572 | 70 | 70 | 0 |  |  | 0
STAIRWAY | 2 | 3"-94 | U |  | 83.6355 | 78 | 85 | 7 | 0.144 | ↑ | 84.3046 |  | 84.3046 | 70 | 70 | 0 |  |  | 0
TRUNK | 2 | 3"-94 | U | 1 m x 1.9 m | 20.4514 | 78 | 120 | 42 | 0.144 | ↑ | 123.6901 |  | 123.6901 | 70 | 70 | 0 |  |  | 0
VOID | 2 | 3"-94 | U |  | 69.7501 | 78 | 120 | 42 | 0.144 | ↑ | 421.8484 |  | 421.8484 | 70 | 70 | 0 |  |  | 0
CHIEF ENGINEER TOILET | 2 | 3"-94 | U | 2.2 m x 1.4 m | 33.1528 | 78 | 85 | 7 | 0.144 | ↑ | 33.418 |  | 33.418 | 70 | 70 | 0 |  |  | 0
1ST ENGINEER TOILET | 2 | 3"-94 | U |  | 6.6306 | 78 | 85 | 7 | 0.144 | ↑ | 6.6836 |  | 6.6836 | 70 | 70 | 0 |  |  | 0
OUTDOOR SPACE | 1 | 3"-94 | D |  | 6.6306 | 78 | 95 | 17 | 0.171 | ↓ | 19.275 |  | 19.275 | 70 | 70 | 0 |  |  | 0
TRANSMISSION SUBTOTAL | [12 empty] | 3292.6167 | [5 empty] | 0
WINDOW |  |  |  |  | 2797434.2406 | [5 empty] | 17483.964 |  | 17483.964
LIGHTS | 7 |  |  |  | 1883.5749 | [5 empty] | 30137.1978 |  | 30137.1978
PERSONNEL | 9 | [9 empty] | 1260 | 1940 | 3200
INFILTRATION
TOTAL | [10 empty] | 52173.7785 | 1940 | 54113.7785 | [5 empty] | 0
TOTAL | [5 empty] | 54113.7785
|  |  |  | ΔT = | 25 | °F
|  |  |  | OCCUPANCY | 15
|  |  |  | Sq. ft. | 1883.5749 | sq. ft
|  |  |  | HEIGHT | 8.8583 | ft
|  |  |  | VOLUME | 16685.2109 | cb. ft
|  |  |  | R/C | 556.1737 | CFM
|  |  |  | qS TOTAL | 52173.7785 | Btu/hr
|  |  |  | qL TOTAL | 1940 | Btu/hr
|  |  |  | qT TOTAL | 54113.7785 | Btu/hr
|  |  |  | qW TOTAL | 0 | Btu/hr
|  |  |  | Q | 1932.3622 | CFM
|  |  |  | Q | 1933 | CFM
|  |  |  | Q (kW) | 0.56651 | kW
|  |  |  | SHF | 0.96415
SYMBOLS |  |  |  | KEY |  | HEATING AND COOLING LOAD CALCULATION
A = Boundary Area | [ft2] | U = Heat Transfer Coefficient | [Btu/ft2/hr/°F] | 1 = Deck Over | 6 = Inboard Bulkhead
qS = Heat Load, Sensible | [Btu/hr] | TO = Temperature of | [°F] | 2 = Deck Under | 7 = Lights
qL = Heat Load, Latent | [Btu/hr] | Adjacent Space / Outside |  | 3 = Outboard Bulkhead / Shell | 8 = Equipment
qT = Heat Load, Total | [Btu/hr] | Td = Temperature Difference | [°F] | 4 = Forward Bulkhead | 9 = Personnel
qW = Heat Load, Winter | [Btu/hr] |  |  | 5 = After Bulkhead
Q = Volumetric Flow Rate | [CFM]
R/C = Rate of Air Change | [CFM]
CALCULATED BY: |  |  | CHECKED BY: |  |  | HULL OR JOB NO.:
[6 empty] | REV. |  |  |  | SHEET NO. | [6 empty] | OF

## DUCTING
SPACE | SPACE NO | DECK | FRAMES | SIDE | BTU/HR |  |  | SHF | OUTSIDE AIR BASED |  |  | CFM | R/C TOTAL AIR | AIR QUANTITY (L/s) | FRICTION LOSS (Pa/mm) | DUCT DIAMETER (mm) | RECT. DUCT SIZE (mm) | Ukuran Diffuser | l/s | JUMLAH DIFFUSER
[5 empty] | SENS. | LATENT | TOTAL |  | R/C | PERS. | EXH. | [5 empty] | L x W
Vegetable Store |  | MAIN DECK | [5 empty] | 0.97097 | 48.7788 | 15 | 15 | 638 | 48.7788 | 301.1025
Meat/Fish Store | [7 empty] | 0 | 33.3723 | 15 | 15 | 325 | 33.3723 | 153.3829
Engine Control Room | [7 empty] | 0.96992 | 208.148 | 30 | 30 | 1738 | 208.148 | 820.2447
Dry Provision Store | [7 empty] | 0.98837 | 153.4453 | 15 | 15 | 1527 | 153.4453 | 720.6638
Cargo Control Room |  | POOP DECK | [5 empty] | 0.85676 | 75.2625 | 15 | 15 | 215 | 75.2625 | 101.4687
Ship Office | [7 empty] | 0.89484 | 94.0146 | 15 | 15 | 306 | 94.0146 | 144.4159
Deck Change Room | [7 empty] | 0.697 | 19.8327 | 15 | 15 | 166 | 19.8327 | 78.3433
Galley | [7 empty] | 0.70398 | 88.7386 | 30 | 30 | 1408 | 88.7386 | 664.502
Crew Mess | [7 empty] | 0.77427 | 119.3776 | 75 | 75 | 697 | 119.3776 | 328.9474
Office Mess | [7 empty] | 0.77427 | 115.8814 | 75 | 75 | 478 | 115.8814 | 225.5909
Motorman 2 Cabin |  | A DECK | [5 empty] | 0.85796 | 41.191 | 15 | 15 | 109 | 41.191 | 51.4423
Motorman 1 Cabin | [7 empty] | 0.84943 | 39.6336 | 15 | 15 | 102 | 39.6336 | 48.1386
AB 2 Cabin | [7 empty] | 0.79945 | 46.1809 | 15 | 15 | 72 | 46.1809 | 33.9802
AB 1 Cabin | [7 empty] | 0.83676 | 45.6088 | 15 | 15 | 93 | 45.6088 | 43.8911
Hospital | [7 empty] | 0.86691 | 54.6353 | 15 | 15 | 118 | 54.6353 | 55.6898
OS Cabin | [7 empty] | 0.85043 | 39.6336 | 15 | 15 | 103 | 39.6336 | 48.6106
Messman Cabin | [7 empty] | 0.78523 | 39.6336 | 15 | 15 | 66 | 39.6336 | 31.1485
Fitter Cabin | [7 empty] | 0.80183 | 42.7484 | 15 | 15 | 73 | 42.7484 | 34.4522
Suez Crew Room | [7 empty] | 0.67166 | 42.9708 | 45 | 45 | 221 | 45 | 104.3004
2nd Engineer Cabin |  | B DECK | [5 empty] | 0.88297 | 71.671 | 15 | 15 | 136 | 71.671 | 64.1849 | 2.2
3rd Engineer Cabin | [7 empty] | 0.83478 | 48.0879 | 15 | 15 | 91 | 48.0879 | 42.9472
Electrician Crew Cabin | [7 empty] | 0.80848 | 11.4419 | 15 | 15 | 76 | 15 | 35.868
Bosun Crew Cabin | [7 empty] | 0.87783 | 49.7089 | 15 | 15 | 130 | 49.7089 | 61.3532
Owner Cabin | [7 empty] | 0.90274 | 60.1655 | 15 | 15 | 167 | 60.1655 | 78.8152
GYM ROOM | [7 empty] | 0.81742 | 262.7411 | 30 | 30 | 242 | 262.7411 | 114.2113
2ND OFFICER CABIN | [7 empty] | 0.90688 | 69.1284 | 15 | 15 | 175 | 69.1284 | 82.5908
3RD OFFICER CABIN | [7 empty] | 0.83478 | 48.0879 | 15 | 15 | 91 | 48.0879 | 42.9472
PUMPMAN CABIN | [7 empty] | 0.85724 | 48.0879 | 15 | 15 | 108 | 48.0879 | 50.9703
COOKMAN CABIN | [7 empty] | 0.88515 | 49.7089 | 15 | 15 | 139 | 49.7089 | 65.6007
MASTER CABIN |  | C DECK | [5 empty] | 0.86755 | 61.0873 | 15 | 15 | 118 | 61.0873 | 55.6898
MASTER BEDROOM | [7 empty] | 0.73275 | 25.6093 | 15 | 15 | 50 | 25.6093 | 23.5974
Chief Officer Cabin | [7 empty] | 0.87798 | 57.9089 | 15 | 15 | 130 | 57.9089 | 61.3532
Chief Officer Bedroom | [7 empty] | 0.77849 | 26.5707 | 15 | 15 | 64 | 26.5707 | 30.2046
Pilot Cabin | [7 empty] | 0.84535 | 43.098 | 15 | 15 | 99 | 43.098 | 46.7228
Office Room | [7 empty] | 0.62505 | 95.7468 | 15 | 15 | 240 | 95.7468 | 113.2674
1st Engineer Cabin | [7 empty] | 0.85497 | 57.9089 | 15 | 15 | 106 | 57.9089 | 50.0264
1st Engineer Bedroom | [7 empty] | 0.82565 | 26.5707 | 15 | 15 | 86 | 26.5707 | 40.5875
Chief Engineer Cabin |  |  |  |  | 3393.6442 |  | 3817.2282 | 0.88903 | 61.0873 | 15 | 15 | 126 | 61.0873 | 59.4654
Chief Engineer Bedroom |  |  |  |  | 2352.2264 |  | 2837.2264 | 0.82906 | 25.6093 | 15 | 15 | 88 | 25.6093 | 41.5314
WHEEL HOUSE |  | BRIDGE DECK |  |  | 52173.7785 |  | 54113.7785 | 0.96415 | 556.1737 | 45 | 45 | 1933 | 556.1737 | 912.2744
TOTAL | [11 empty] | 12850 |  | 6064.5247
|  | MAIN DECK | [9 empty] | 4228 |  | 1995.3938
|  | POOP DECK | [9 empty] | 3270 |  | 1543.2682
|  | A DECK | [9 empty] | 957 |  | 451.6537
|  | B DECK | [9 empty] | 1355 |  | 639.4888
|  | C DECK | [9 empty] | 1107 |  | 522.4458
|  | BRIDGE DECK | [9 empty] | 1933 |  | 912.2744
|  | SECTION A | 736 |  | SECTION A (A DECK tanpa Suez Crew Room)
|  | Ducting B | 1355
|  | Ducting C | 1107 |  | Ducting C (seluruh ruangan C Deck)
|  | Ducting D | 1933 |  | 5131
|  | Ducting E | 2386
|  | Ducting F | 1408
|  | Ducting G | #REF! |  | #REF!
| Min. | [6 empty] | at least max
Total Air Quantity = | 12850 | CFM | [5 empty] | 19275 |  |  |  | CFM
Total Air Quantity = | 6064.5247 | L/s | [5 empty] | 9096.7871 |  |  |  | L/s
Total Air Quantity = | 21832.289 | m3/h | [5 empty] | 32748.4336 |  |  |  | m3/h
Total Air Quantity = | 6.0645 | m3/s | [5 empty] | 9.0968 |  |  |  | m3/s
Ukuran ruang AHU
Height : | 2.7 | m
Width : | 5 | m
Length : | 5.6 | m
Pilihan 1
Merk AHU : | TRANE
Tipe : | Unit Size 40
Link : | https://www.trane.com/content/dam/Trane/Commercial/lar/es/product-systems/Sistemas-de-agua-helada/Performance-climate-changer/CSAA/Catalogo/CLCH-PRC022-EN_092013_Performance%20Air%20Handler%20Catalog.pdf
Speed : | 500 | fpm
Airflow : | 20000 | CFM
| 25519 | CFM | [5 empty] | at 625 fpm
Height : | 67.25 | in
| 1.7081 | m | [5 empty] | Memenuhi
Width : | 112.5 | in
| 2.8575 | m | [5 empty] | Memenuhi
Length : | 96 | in
| 2.4384 | m | [5 empty] | Memenuhi
Pilihan 2
Merk AHU : | TRANE
Tipe : | CLCP 035
Link : | https://www.tranehk.com/files/Products/CLCH-PRC010B-EN_0619(English).pdf
Speed : | 590.5512 | fpm | [5 empty] | 3 |  |  |  | m/s
Airflow : | 34000 | m3/h | [5 empty] | 36396 |  |  |  | m3/h
| 20011.6442 | CFM
Height : |  | in
| 2.108 | m | [5 empty] | Memenuhi
Width : |  | in
| 2.298 | m | [5 empty] | Memenuhi
Length : |  | in
| 8.215 | m | [5 empty] | tidak memenuhi
| Mixing box/intake section | 465 | [5 empty] | mm
| Per-filter section | 155 | [5 empty] | mm
| Secondary filter section | 465 | [5 empty] | mm
| Flat + Bag Filter section | 620 | [5 empty] | mm
| Cooling Coil section | 465 | [5 empty] | mm
| Hot water coil section | 465 | [5 empty] | mm
| Steam coil section | 310 | [5 empty] | mm
| Electric heater section | 465 | [5 empty] | mm
| Steam humidifier section | 775 | [5 empty] | mm
| Film humidifier section | 465 | [5 empty] | mm
| High-pressure atomizing humidifier section (include drop eliminator) | 1240 | [5 empty] | mm
| Fan section | [6 empty] | mm
| Sound Attenuator section | [6 empty] | mm
| Hi-capacity filter section | 620 | [5 empty] | mm
| Access section | 620 | [5 empty] | mm
| Supply airflow section | 465 | [5 empty] | mm
| Heat wheel section | 620 | [5 empty] | mm
|  | 8215 | [5 empty] | mm
|  | 8.215 | [5 empty] | m
Horizontal Unit: Fan Outlet Position & Unit Dimension
| Tipe : | Position 1
| A + B : | 1534
Pilihan 3
Merk AHU : | TRANE
Tipe : | Unit Size 40
Link : | https://www.trane.com/content/dam/Trane/Commercial/lar/es/product-systems/Sistemas-de-agua-helada/Performance-climate-changer/CSAA/Catalogo/CLCH-PRC022-EN_092013_Performance%20Air%20Handler%20Catalog.pdf
Speed : | 500 | fpm
Airflow : | 20000 | CFM
| 25519 | CFM | [5 empty] | at 625 fpm
Height : | 67.25 | in
| 1.7081 | m | [5 empty] | Memenuhi
Width : | 112.5 | in
| 2.8575 | m | [5 empty] | Memenuhi
Length : | 96 | in
| 2.4384 | m | [5 empty] | Memenuhi
Weight : |  | kg
Pilihan 4
Merk AHU : | DAIKIN
Tipe : | PROFESSIONAL 13
Link : | https://industri.daikin.no/wp-content/uploads/2020/06/2020_04_Produktkatalog_Air_Handling_Ventilation.pdf?utm_source=chatgpt.com
Speed : |  | fpm
Airflow : | 33800 | m3/h
Height : |  | in
| 1.87 | m | [5 empty] | Memenuhi
Width : |  | in
| 2.51 | m | [5 empty] | Memenuhi
Length : |  | in
|  | m | [5 empty] | Memenuhi
Weight : |  | kg
Pilihan 5
Merk AHU : | DAIKIN
Tipe : | 62M
Link : | https://www.daikin.com.sg/resources/ck/files/catalogue/Air%20Handling%20Unit%20%28AH%20Models%29.pdf?utm_source=chatgpt.com
Speed : | 500 | fpm
Airflow : | 24000 | CFM
Height : |  | in
| 1.9 | m | [5 empty] | Memenuhi
Width : |  | in
| 3.8 | m | [5 empty] | Memenuhi
Length : |  | in
| 2.35 | m | [5 empty] | Memenuhi
Weight : |  | kg
Pilihan 6
Merk AHU : | Teknotherm
Tipe : | CECE280 | 2500 Pa
Link : | https://www.teknotherm.no/wp-content/uploads/2015/11/73-11_air_handling_unit_2013.pdf
Speed : | 500 | fpm
Airflow : | 24000 | m3/h
Height : | 14125.8665 | CFM
in
Width : | 1.9 | m | [5 empty] | Memenuhi
in
Length : | 3.8 | m | [5 empty] | Memenuhi
in
Weight : | 2.35 | m | [5 empty] | Memenuhi
kg
Pilihan 7
Merk AHU : | AERON
Tipe : | CECE280 | 2500Oa
Link : | https://www.teknotherm.no/wp-content/uploads/2015/11/73-11_air_handling_unit_2013.pdf
Speed : | 500 | fpm
Airflow : | 24000 | CFM
Height :
in
Width : | 1.9 | m | [5 empty] | Memenuhi
in
Length : | 3.8 | m | [5 empty] | Memenuhi
in
Weight : | 2.35 | m | [5 empty] | Memenuhi
kg

## STATIC REGAIN
DUCTING A
CFM
|  | AB 1 | 93
|  | Fitter | 73
|  | Messman | 66
|  | OS | 103
|  | Motorman 1 | 102
|  | Motorman 2 | 109
|  | AB 2 | 72
|  | Hospital | 118
|  | Engine Control Room | 1738
2474
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  |  | 10
DECK | RUANG | BRANCH SECT. NO. | AIR QUANTITY Q (cfm) | EQUIV. DUCT LENGTH L (ft) | PRESSURE READING (in. wg) |  | TAKE-OFF TO TAKE-OFF S.P. CHANCE (in.wg) | S.P. AHEAD OF TAKE-OFF (in. wg) | AIR TERMINAL PRESS (in. wg) | DUCT DIAMETR SIZE (in) | DUCT SIZE (mm) |  | VELOCITY V (fpm) | VELOCITY V (fps) | Panjang Line (m) | Panjang Line (ft) | f | Le = (K*D)/f [in] | Le = (K*D)/f [ft] | Le Tee 8 in | Friction Loss (in.wg) | Pressure Loss (in.wg) | Jarak antar Tee (6*D)
[5 empty] | Initial | Selected
A DECK |  | DUCTING 1-01-02 | 2474 | 18.04 |  |  | 1.5 | 1.8428 | 1.5 | 12 | 304.8 |  | 4400 | 73.3333 | 5.5 | 18.04 | 3.96 | 3.0303 | 9.9394 |  | 1.9 | 0.34276 | 1.8288
0.34276
A DECK |  | AD 02-0201 | 166 | 1.64 | 1.5 | 0.86 | 0.64 | 1.2028 | 1.5 | 4 | 101.6 |  | 2800 | 46.6667 | 0.5 | 1.64 | 3.96 | 1.0101 | 3.3131 |  | 3.3 | 0.05412 | 0.6096
A DECK |  | AD 0201-020101 | 93 | 10.216 | 1.4 | 0.84 | 0.56 | 0.64276 | 1.5 | 4 | 101.6 |  | 1500 | 25 | 2.2 | 10.216 | 3.96 | 1.0101 | 3.3131 |  | 1.1 | 0.11238 | 0.6096
A DECK |  | AD 0201-020102 | 73 | 21.04 | 0.155 | 0.155 | 0 | 0.64276 | 1.5 | 4 | 101.6 |  | 1300 | 21.6667 | 5.5 | 21.04 | 3.96 | 1.0101 | 3.3131 |  | 0.65 | 0.13676 | 0.6096
A DECK |  | AD 02-03 | 2308 | 23.48 | 1.4 | 1.4 | 0 | 1.8428 | 1.5 | 12 | 304.8 |  | 4200 | 70 | 3.5 | 23.48 | 3.96 | 3.0303 | 9.9394 |  | 1.8 | 0.42264 | 1.8288
A DECK |  | AD 03-0301 | 66 | 9.84 | 1.2 | 1.2 | 0 | 1.8428 | 1.5 | 3 | 76.2 |  | 2000 | 33.3333 | 3 | 9.84 | 3.96 | 0.75758 | 2.4848 |  | 2.9 | 0.28536 | 0.4572
A DECK |  | AD 03-04 | 3100 | 7.872 | 1.25 | 1.25 | 0 | 1.8428 | 1.5 | 12 | 304.8 |  | 3900 | 65 | 2.4 | 7.872 | 3.96 | 3.0303 | 9.9394 |  | 1.5 | 0.11808 | 1.8288
A DECK |  | AD 04-0401 | 103 | 9.84 | 1 | 0.34 | 0.66 | 1.1828 | 1.5 | 4 | 101.6 |  | 1550 | 25.8333 | 3 | 9.84 | 3.96 | 1.0101 | 3.3131 |  | 1.3 | 0.12792 | 0.6096
A DECK |  | AD 04-05 | 2900 | 8.2 | 1.05 | 1.05 | 0 | 1.8428 | 1.5 | 12 | 304.8 |  | 3700 | 61.6667 | 2.5 | 8.2 | 3.96 | 3.0303 | 9.9394 |  | 1.4 | 0.1148 | 1.8288
A DECK |  | AD 05-06 | 401 | 1.968 | 0.95 | 0.85 | 0.1 | 1.7428 | 1.5 | 6 | 152.4 |  | 3000 | 50 | 0.6 | 1.968 | 3.96 | 1.5152 | 4.9697 |  | 2.2 | 0.043296 | 0.9144
A DECK |  | AD 06-0601 | 102 | 9.84 | 0.61 | 0.34 | 0.27 | 1.4728 | 1.5 | 4 | 101.6 |  | 1550 | 25.8333 | 3 | 9.84 | 3.96 | 1.0101 | 3.3131 |  | 1.3 | 0.12792 | 0.6096
A DECK |  | AD 06-07 | 299 | 6.888 | 0.62 | 0.48 | 0.14 | 1.6028 | 1.5 | 6 | 152.4 |  | 2200 | 36.6667 | 2.1 | 6.888 | 3.96 | 1.5152 | 4.9697 |  | 1.4 | 0.096432 | 0.9144
A DECK |  | AD 07-0701 | 109 | 13.448 | 0.3 | 0.16 | 0.14 | 1.4628 | 1.5 | 5 | 127 |  | 1200 | 20 | 4.1 | 13.448 | 3.96 | 1.2626 | 4.1414 |  | 0.52 | 0.06993 | 0.762
A DECK |  | AD 07-08 | 190 | 9.184 | 0.33 | 0.21 | 0.12 | 1.4828 | 1.5 | 6 | 152.4 |  | 1410 | 23.5 | 2.8 | 9.184 | 3.96 | 1.5152 | 4.9697 |  | 0.55 | 0.050512 | 0.9144
A DECK |  | AD 08-0801 | 72 | 3.936 | 1.25 | 0.68 | 0.57 | 0.91276 | 1.5 | 5 | 127 |  | 1000 | 16.6667 | 1.2 | 3.936 | 3.96 | 1.2626 | 4.1414 |  | 0.38 | 0.014957 | 0.762
A DECK |  | AD 08-0802 | 118 | 10.496 | 1.25 | 0.85 | 0.4 | 0.51276 | 1.5 | 6 | 152.4 |  | 1000 | 16.6667 | 3.2 | 10.496 | 3.96 | 1.5152 | 4.9697 |  | 0.32 | 0.033587 | 0.9144
A DECK |  | AD 05-09 | 1738 | 11.808 | 0.95 | 0.8 | 0.15 | 1.6928 | 1.5 | 12 | 304.8 |  | 3200 | 53.3333 | 3.6 | 11.808 | 3.96 | 3.0303 | 9.9394 |  | 1 | 0.11808 | 1.8288
A DECK-MAIN DECK |  | AD 09-MD 09 | 1738 | 17.384 | 0.65 | 0.45 | 0.2 | 1.4928 | 1.5 | 14 | 355.6 |  | 2400 | 40 | 5.3 | 17.384 | 3.96 | 3.5354 | 11.596 |  | 0.5 | 0.08692 | 2.1336
MAIN DECK |  | MD 09-10 | 1738 | 11.808 | 0.65 | 0.45 | 0.2 | 1.2928 | 1.5 | 14 | 355.6 |  | 2200 | 36.6667 | 3.6 | 11.808 | 3.96 | 3.5354 | 11.596 |  | 0.45 | 0.053136 | 2.1336
MAIN DECK |  | MD 10-1001 | 638.75 | 9.512 | 0.33 | 0.31 | 0.02 | 1.2728 | 1.5 | 8 | 203.2 |  | 1850 | 30.8333 | 2.9 | 9.512 | 3.96 | 2.0202 | 6.6263 |  | 0.7 | 0.066584 | 1.2192
MAIN DECK |  | MD 1001-100101 | 319.375 | 2.624 | 0.23 | 0.14 | 0.09 | 1.1828 | 1.5 | 7 | 177.8 |  | 1200 | 20 | 0.8 | 2.624 | 3.96 | 1.7677 | 5.798 |  | 0.35 | 0.009184 | 1.0668
MAIN DECK |  | MD 1001-100102 | 319.375 | 2.624 | 0.23 | 0.14 | 0.09 | 1.1828 | 1.5 | 7 | 177.8 |  | 1200 | 20 | 0.8 | 2.624 | 3.96 | 1.7677 | 5.798 |  | 0.35 | 0.009184 | 1.0668
MAIN DECK |  | MD 10-1002 | 638.75 | 17.712 | 0.33 | 0.33 | 0 | 1.2928 | 1.5 | 8 | 203.2 |  | 1850 | 30.8333 | 5.4 | 17.712 | 3.96 | 2.0202 | 6.6263 |  | 0.7 | 0.12398 | 1.2192
MAIN DECK |  | MD 1002-100201 | 319.375 | 2.624 | 0.23 | 0.14 | 0.09 | 1.2028 | 1.5 | 7 | 177.8 |  | 1200 | 20 | 0.8 | 2.624 | 3.96 | 1.7677 | 5.798 |  | 0.35 | 0.009184 | 1.0668
MAIN DECK |  | MD 1002-102002 | 319.375 | 2.624 | 0.23 | 0.14 | 0.09 | 1.2028 | 1.5 | 7 | 177.8 |  | 1200 | 20 | 0.8 | 2.624 | 3.96 | 1.7677 | 5.798 |  | 0.35 | 0.009184 | 1.0668
MAIN DECK |  | MD 10-11 | 1277.5 | 8.364 | 0.33 | 0.31 | 0.02 | 1.2728 | 1.5 | 11 | 279.4 |  | 2000 | 33.3333 | 2.55 | 8.364 | 3.96 | 2.7778 | 9.1111 |  | 0.5 | 0.04182 | 1.6764
MAIN DECK |  | MD 11-12 | 638.75 | 2.952 | 0.26 | 0.175 | 0.085 | 1.1878 | 1.5 | 9 | 228.6 |  | 1450 | 24.1667 | 0.9 | 2.952 | 3.96 | 2.2727 | 7.4545 |  | 0.38 | 0.011218 | 1.3716
MAIN DECK |  | MD 12-1201 | 319.375 | 2.624 | 0.14 | 0.14 | 0 | 1.1878 | 1.5 | 7 | 177.8 |  | 1200 | 20 | 0.8 | 2.624 | 3.96 | 1.7677 | 5.798 |  | 0.35 | 0.009184 | 1.0668
MAIN DECK |  | MD 12-1202 | 319.375 | 2.624 | 0.14 | 0.14 | 0 | 1.1878 | 1.5 | 7 | 177.8 |  | 1200 | 20 | 0.8 | 2.624 | 3.96 | 1.7677 | 5.798 |  | 0.35 | 0.009184 | 1.0668
MAIN DECK |  | MD 11-1101 | 638.75 | 17.712 | 0.242 | 0.175 | 0.067 | 1.2058 | 1.5 | 9 | 228.6 |  | 1450 | 24.1667 | 5.4 | 17.712 | 3.96 | 2.2727 | 7.4545 |  | 0.38 | 0.067306 | 1.3716
MAIN DECK |  | MD 1101-110101 | 319.375 | 2.624 | 0.14 | 0.14 | 0 | 1.2058 | 1.5 | 7 | 177.8 |  | 1200 | 20 | 0.8 | 2.624 | 3.96 | 1.7677 | 5.798 |  | 0.35 | 0.009184 | 1.0668
MAIN DECK |  | MD 1101-110102 | 319.375 | 2.624 | 0.14 | 0.14 | 0 | 1.2058 | 1.5 | 7 | 177.8 |  | 1200 | 20 | 0.8 | 2.624 | 3.96 | 1.7677 | 5.798 |  | 0.35 | 0.009184 | 1.0668
DUCTING B
CFM
|  | 2nd Engineer Cabin | 136
|  | 3rd Engineer Cabin | 91
|  | Electrician Crew Cabin | 76
|  | Bosun Crew Cabin | 130
|  | Owner Cabin | 167
|  | GYM ROOM | 242
|  | 2ND OFFICER CABIN | 175
|  | 3RD OFFICER CABIN | 91
|  | PUMPMAN CABIN | 108
|  | COOKMAN CABIN | 139
1355
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  |  | 10
DECK | RUANG | BRANCH SECT. NO. | AIR QUANTITY Q (cfm) | EQUIV. DUCT LENGTH L (ft) | PRESSURE READING (in. wg) |  | TAKE-OFF TO TAKE-OFF S.P. CHANCE (in.wg) | S.P. AHEAD OF TAKE-OFF (in. wg) | AIR TERMINAL PRESS (in. wg) | DUCT SIZE (in) | DUCT SIZE (mm) |  | VELOCITY V (fpm) | VELOCITY V (fps) | Panjang Line (m) | Panjang Line (ft) | f | Le = (K*D)/f [in] | Le = (K*D)/f [ft] | Le Tee 8 in | Friction Loss (in.wg) | Pressure Loss (in.wg) | Jarak antar Tee (6*D)
[5 empty] | Initial | Selected
A DECK |  | DUCTING 02-01 | 1355 | 10.496 |  |  | 1.5 | 1.7939 | 1.5 | 9 | 228.6 |  | 5000 | 83.3333 | 3.2 | 10.496 | 3.96 | 2.2727 | 7.4545 |  | 2.8 | 0.29389 | 1.3716
|  | 1355 6: 0.29389 |  |  |  | 0
A DECK |  | AD 01-02 | 1992 | 40.672 | 0.89 | 0.75 | 0.14 | 1.6539 | 1.5 | 11 | 279.4 |  | 3050 | 50.8333 | 12.4 | 40.672 | 3.96 | 2.7778 | 9.1111 |  | 1.1 | 0.44739 | 1.6764
0
A DECK-B DECK |  | AD 02-BD 02 | 1992 | 8.856 | 0.65 | 0.55 | 0.1 | 1.5539 | 1.5 | 12 | 304.8 |  | 2600 | 43.3333 | 2.7 | 8.856 | 3.96 | 3.0303 | 9.9394 |  | 0.7 | 0.061992 | 1.8288
B DECK |  | BD 02-03 | 1992 | 3.116 | 0.45 | 0.285 | 0.165 | 1.3889 | 1.5 | 14 | 355.6 |  | 1950 | 32.5 | 0.95 | 3.116 | 3.96 | 3.5354 | 11.596 |  | 0.35 | 0.010906 | 2.1336
B DECK |  | BD 03-031 | 433 | 11.48 | 0.24 | 0.18 | 0.06 | 1.3289 | 1.5 | 9 | 228.6 |  | 1480 | 24.6667 | 3.5 | 11.48 | 3.96 | 2.2727 | 7.4545 |  | 0.38 | 0.043624 | 1.3716
B DECK |  | BD 031-0312 | 206 | 9.512 | 0.138 | 0.128 | 0.01 | 1.3189 | 1.5 | 7 | 177.8 |  | 1150 | 19.1667 | 2.9 | 9.512 | 3.96 | 1.7677 | 5.798 |  | 0.34 | 0.032341 | 1.0668
B DECK |  | BD 0312-03121 | 76 | 1.968 | 0.085 | 0.075 | 0.01 | 1.3089 | 1.5 | 5 | 127 |  | 1000 | 16.6667 | 0.6 | 1.968 | 3.96 | 1.2626 | 4.1414 |  | 0.4 | 0.007872 | 0.762
B DECK |  | BD 0312-03122 | 130 | 11.48 | 0.085 | 0.06 | 0.025 | 1.2939 | 1.5 | 7 | 177.8 |  | 1000 | 16.6667 | 3.5 | 11.48 | 3.96 | 1.7677 | 5.798 |  | 0.28 | 0.032144 | 1.0668
B DECK |  | BD 031-0311 | 227 | 5.248 | 0.145 | 0.09 | 0.055 | 1.2739 | 1.5 | 8 | 203.2 |  | 1000 | 16.6667 | 1.6 | 5.248 | 3.96 | 2.0202 | 6.6263 |  | 0.25 | 0.01312 | 1.2192
B DECK |  | BD 0311-03111 | 91 | 1.968 | 0.06 | 0.06 | 0 | 1.2739 | 1.5 | 6 | 152.4 |  | 1000 | 16.6667 | 0.6 | 1.968 | 3.96 | 1.5152 | 4.9697 |  | 0.3 | 0.005904 | 0.9144
B DECK |  | BD 0311-03112 | 136 | 11.808 | 0.06 | 0.06 | 0 | 1.2739 | 1.5 | 7 | 177.8 |  | 1000 | 16.6667 | 3.6 | 11.808 | 3.96 | 1.7677 | 5.798 |  | 0.28 | 0.033062 | 1.0668
B DECK |  | BD 03-04 | 922 | 32.472 | 0.21 | 0.13 | 0.08 | 1.3089 | 1.5 | 14 | 355.6 |  | 1300 | 21.6667 | 9.9 | 32.472 | 3.96 | 3.5354 | 11.596 |  | 0.18 | 0.05845 | 2.1336
B DECK |  | BD 04-041 | 242 | 4.592 | 0.11 | 0.1 | 0.01 | 1.2989 | 1.5 | 8 | 203.2 |  | 1000 | 16.6667 | 1.4 | 4.592 | 3.96 | 2.0202 | 6.6263 |  | 0.28 | 0.012858 | 1.2192
B DECK |  | BD 04-05 | 680 | 22.96 | 0.95 | 0.068 | 0.882 | 0.42689 | 1.5 | 14 | 355.6 |  | 1000 | 16.6667 | 7 | 22.96 | 3.96 | 3.5354 | 11.596 |  | 0.12 | 0.027552 | 2.1336
B DECK |  | BD 05-051 | 139 | 5.248 | 0.06 | 0.06 | 0 | 0.42689 | 1.5 | 7 | 177.8 |  | 1000 | 16.6667 | 1.6 | 5.248 | 3.96 | 1.7677 | 5.798 |  | 0.28 | 0.014694 | 1.0668
B DECK |  | BD 05-06 | 541 | 7.544 | 0.06 | 0.06 | 0 | 0.42689 | 1.5 | 14 | 355.6 |  | 1000 | 16.6667 | 2.3 | 7.544 | 3.96 | 3.5354 | 11.596 |  | 0.12 | 0.0090528 | 2.1336
B DECK |  | BD 06-061 | 108 | 2.952 | 0.06 | 0.06 | 0 | 0.42689 | 1.5 | 7 | 177.8 |  | 1000 | 16.6667 | 0.9 | 2.952 | 3.96 | 1.7677 | 5.798 |  | 0.28 | 0.0082656 | 1.0668
B DECK |  | BD 06-07 | 433 | 11.48 | 0.06 | 0.06 | 0 | 0.42689 | 1.5 | 12 | 304.8 |  | 1000 | 16.6667 | 3.5 | 11.48 | 3.96 | 3.0303 | 9.9394 |  | 0.14 | 0.016072 | 1.8288
B DECK |  | BD 07-071 | 91 | 2.952 | 0.06 | 0.06 | 0 | 0.42689 | 1.5 | 6 | 152.4 |  | 1000 | 16.6667 | 0.9 | 2.952 | 3.96 | 1.5152 | 4.9697 |  | 0.3 | 0.008856 | 0.9144
B DECK |  | BD 07-08 | 342 | 9.512 | 0.06 | 0.06 | 0 | 0.42689 | 1.5 | 11 | 279.4 |  | 1000 | 16.6667 | 2.9 | 9.512 | 3.96 | 2.7778 | 9.1111 |  | 0.15 | 0.014268 | 1.6764
B DECK |  | BD 08-081 | 175 | 9.84 | 0.06 | 0.06 | 0 | 0.42689 | 1.5 | 8 | 203.2 |  | 1000 | 16.6667 | 3 | 9.84 | 3.96 | 2.0202 | 6.6263 |  | 0.15 | 0.01476 | 1.2192
B DECK |  | BD 08-09 | 91 | 24.928 | 0.06 | 0.06 | 0 | 0.42689 | 1.5 | 7 | 177.8 |  | 1000 | 16.6667 | 7.6 | 24.928 | 3.96 | 1.7677 | 5.798 |  | 0.28 | 0.069798 | 1.0668
Ducting C (C Deck)
CFM
|  | Pilot Cabin | 99
|  | Chief Officer Bedroom | 64
|  | Chief Officer Cabin | 130
|  | Master Bedroom | 50
|  | Master Cabin | 118
|  | Office | 240
|  | 1st engineer bedroom | 86
|  | 1st engineer cabin | 106
|  | Chief engineer bedroom | 88
|  | Chief Engineer Cabin | 126
1107
DECK | Posisi diffusser | BRANCH SECT. NO. | AIR QUANTITY Q (cfm) | EQUIV. DUCT LENGTH L (ft) | PRESSURE READING (in. wg) |  | TAKE-OFF TO TAKE-OFF S.P. CHANCE (in.wg) | S.P. AHEAD OF TAKE-OFF (in. wg) | AIR TERMINAL PRESS (in. wg) | DUCT SIZE (in) | DUCT SIZE diameter (mm) | DUCT SIZE radius (m) | VELOCITY V (fpm) | VELOCITY V (fps) | Panjang Line (m) | Panjang Line (ft) | f | Le = (K*D)/f [in] | Le = (K*D)/f [ft] | Le Tee 8 in | Friction Loss (in.wg) | Pressure Loss (in.wg) | Jarak antar Tee (6*D) | Pipe Flow Expert
|  | 1355 4: Initial; 1355 5: Selected | [13 empty] | DUCT SIZE diameter (in) | DUCT SIZE diameter (in) % | DUCT SIZE diameter (in) % | CFM | CFM Error % | CFM Error % | VELOCITY V (fps) | VELOCITY (fps) Error % | VELOCITY (fps) Error %
A DECK-C DECK |  | DUCTING C-AD 01 - C-CD 09 | 1107 | 60.6823 |  |  | 1.5 | 1.8338 | 1.5 | 10 | 254 | 0.127 | 2000 | 33.3333 | 18.5007 | 60.6823 | 3.96 | 2.5253 | 8.2828 |  | 0.55 | 0.33375 | 1.524 | 10 | 0 | 0 | 1107 | 0 | 0 | 34.795 | 4.385 | 4.385
|  | 1355 6: 0.33375 |  | 0 |  | 0
C DECK |  | C-CD 09-09103 | 646 | 18.5648 |  |  | 0 | 1.8338 | 1.5 | 9 | 228.6 | 0.1143 | 1500 | 25 | 5.66 | 18.5648 | 3.96 | 2.2727 | 7.4545 |  | 1.5 | 0.27847 | 1.3716 | 10 | 11.1111 | 11.1111 | 646 | 0 | 0 | 20.321 | -18.716 | 18.716
C DECK |  | C-CD 09103-091031 | 240 | 2.952 |  |  | 0 |  | 1.5 | 6 | 152.4 | 0.0762 | 1200 | 20 | 0.9 | 2.952 | 3.96 | 1.5152 | 4.9697 |  | 1.5 | 0.04428 | 0.9144 | 4 | -33.3333 | 33.3333 | 248 | 3.3333 | 3.3333 | 48.448 | 142.24 | 142.24
C DECK | Office | C-CD 091031-0910311 | 120 | 2.624 |  |  | 0 |  | 1.5 | 4 | 101.6 | 0.0508 |  | 0 | 0.8 | 2.624 | 3.96 | 1.0101 | 3.3131 |  | 1.5 | 0.03936 | 0.6096 | 4 | 0 | 0 | 124 | 3.3333 | 3.3333
C DECK | Office | C-CD 091031-0910312 | 120 | 2.624 |  |  | 0 |  | 1.5 | 4 | 101.6 | 0.0508 |  | 0 | 0.8 | 2.624 | 3.96 | 1.0101 | 3.3131 |  | 1.5 | 0.03936 | 0.6096 | 4 | 0 | 0 | 124 | 3.3333 | 3.3333
C DECK |  | C-CD 09103-09104 | 406 | 21.156 |  |  | 0 | 0 | 1.5 | 8 | 203.2 | 0.1016 | 1200 | 20 | 6.45 | 21.156 | 3.96 | 2.0202 | 6.6263 |  | 1.5 | 0.31734 | 1.2192 | 8 | 0 | 0 | 397 | -2.2167 | 2.2167 | 19.716 | -1.42 | 1.42
C DECK | Chief Engineer Cabin | C-CD 09104-091041 | 126 | 3.936 |  |  | 0 |  | 1.5 | 4 | 101.6 | 0.0508 |  | 0 | 1.2 | 3.936 | 3.96 | 1.0101 | 3.3131 |  | 1.5 | 0.05904 | 0.6096 | 3 | -25 | 25 | 132 | 4.7619 | 4.7619
C DECK |  | C-CD 09104-09105 | 280 | 7.216 |  |  | 0 | 0 | 1.5 | 8 | 203.2 | 0.1016 | 1000 | 16.6667 | 2.2 | 7.216 | 3.96 | 2.0202 | 6.6263 |  | 1.5 | 0.10824 | 1.2192 | 8 | 0 | 0 | 265 | -5.3571 | 5.3571 | 13.145 | -21.13 | 21.13
C DECK | Chief Engineer Bedroom | C-CD 09105-091051 | 88 | 2.624 |  |  | 0 | 1.8338 | 1.5 | 3 | 76.2 | 0.0381 |  | 0 | 0.8 | 2.624 | 3.96 | 0.75758 | 2.4848 |  | 1.5 | 0.03936 | 0.4572 | 3 | 0 | 0 | 83.98 | -4.5682 | 4.5682
C DECK |  | C-CD 09105-09106 | 192 | 3.936 |  |  | 0 |  | 1.5 | 7 | 177.8 | 0.0889 | 1000 | 16.6667 | 1.2 | 3.936 | 3.96 | 1.7677 | 5.798 |  | 1.5 | 0.05904 | 1.0668 | 8 | 14.2857 | 14.2857 | 181 | -5.7292 | 5.7292 |  | -100 | 100
C DECK | 1st Engineer Cabin | C-CD 09106-091061 | 106 | 2.624 |  |  | 0 | 1.8338 | 1.5 | 4 | 101.6 | 0.0508 |  | 0 | 0.8 | 2.624 | 3.96 | 1.0101 | 3.3131 |  | 1.5 | 0.03936 | 0.6096 | 3.5 | -12.5 | 12.5 | 113 | 6.6038 | 6.6038
C DECK | 1st Engineer Bedroom | C-CD 09106-091071 | 88 | 12.136 |  |  | 0 |  | 1.5 | 3 | 76.2 | 0.0381 |  | 0 | 3.7 | 12.136 | 3.96 | 0.75758 | 2.4848 |  | 1.5 | 0.18204 | 0.4572 | 3 | 0 | 0 | 67.7 | -23.0682 | 23.0682
0 | bar: 1355 3
C DECK |  | C-CD 09-09201 | 461 | 11.4472 |  |  | 0 | 0 | 1.5 | 8 | 203.2 | 0.1016 | 1400 | 23.3333 | 3.49 | 11.4472 | 3.96 | 2.0202 | 6.6263 |  | 1.5 | 0.17171 | 1.2192 | 8 | 0 | 0 | 461 | 0 | 0 |  | -100 | 100
C DECK | Chief Officer Cabin | C-CD 09201-092011 | 130 | 3.936 |  |  | 0 | 0 | 1.5 | 4 | 101.6 | 0.0508 |  | 0 | 1.2 | 3.936 | 3.96 | 1.0101 | 3.3131 |  | 1.5 | 0.05904 | 0.6096 | 4 | 0 | 0 | 133 | 2.3077 | 2.3077
C DECK |  | C-CD 09201-09202 | 163 | 9.184 |  |  | 0 | 0 | 1.5 | 6 | 152.4 | 0.0762 | 1000 | 16.6667 | 2.8 | 9.184 | 3.96 | 1.5152 | 4.9697 |  | 1.5 | 0.13776 | 0.9144 | 6 | 0 | 0 | 156 | -4.2945 | 4.2945 |  | -100 | 100
C DECK | Chief Officer Bedroom | C-CD 09202-092021 | 64 | 3.936 |  |  | 0 | 1.8338 | 1.5 | 3 | 76.2 | 0.0381 |  | 0 | 1.2 | 3.936 | 3.96 | 0.75758 | 2.4848 |  | 1.5 | 0.05904 | 0.4572 | 3 | 0 | 0 | 61.25 | -4.2969 | 4.2969
C DECK | Pilot Cabin | C-CD 09202-092031 | 99 | 13.776 |  |  | 0 | 0 | 1.5 | 4 | 101.6 | 0.0508 |  | 0 | 4.2 | 13.776 | 3.96 | 1.0101 | 3.3131 |  | 1.5 | 0.20664 | 0.6096 | 4 | 0 | 0 | 95.21 | -3.8283 | 3.8283
C DECK |  | C-CD 09201-09204 | 168 | 11.808 |  |  | 0 | 1.8338 | 1.5 | 6 | 152.4 | 0.0762 | 1000 | 16.6667 | 3.6 | 11.808 | 3.96 | 1.5152 | 4.9697 |  | 1.5 | 0.17712 | 0.9144 | 6 | 0 | 0 | 171 | 1.7857 | 1.7857 |  | -100 | 100
C DECK | Master Bedroom | C-CD 09204-092041 | 50 | 3.936 |  |  | 0 | 0 | 1.5 | 3 | 76.2 | 0.0381 |  | 0 | 1.2 | 3.936 | 3.96 | 0.75758 | 2.4848 |  | 1.5 | 0.05904 | 0.4572 | 3 | 0 | 0 | 57.62 | 15.24 | 15.24
C DECK | Master Cabin | C-CD 09204-092051 | 118 | 13.776 |  |  | 0 | 0 | 1.5 | 4 | 101.6 | 0.0508 |  | 0 | 4.2 | 13.776 | 3.96 | 1.0101 | 3.3131 |  | 1.5 | 0.20664 | 0.6096 | 5 | 25 | 25 | 113 | -4.2373 | 4.2373
[25 empty] | -1.0218 | 6.0615 |  | -0.84486 | 4.9148 |  | -32.7379 | 65.3212
SECTION A
|  | Ruangan | CFM
|  | Motorman 2 Cabin | 109
|  | Motorman 1 Cabin | 102
|  | AB 2 Cabin | 72
|  | AB 1 Cabin | 93
|  | Hospital | 118
|  | OS Cabin | 103
|  | Messman Cabin | 66
|  | Fitter Cabin | 73
|  | Total = | 736
DECK | Posisi diffusser | BRANCH SECT. NO. | AIR QUANTITY Q (cfm) | EQUIV. DUCT LENGTH L (ft) | PRESSURE READING (in. wg) |  | TAKE-OFF TO TAKE-OFF S.P. CHANCE (in.wg) | S.P. AHEAD OF TAKE-OFF (in. wg) | AIR TERMINAL PRESS (in. wg) | DUCT SIZE (in) | DUCT SIZE diameter (mm) | DUCT SIZE radius (m) | VELOCITY V (fpm) | VELOCITY V (fps) | Panjang Line (m) | Panjang Line (ft) | f | Le = (K*D)/f [in] | Le = (K*D)/f [ft] | Le Tee 8 in | Friction Loss (in.wg) | Pressure Loss (in.wg) | Jarak antar Tee (6*D) | Pipe Flow Expert | [13 empty] | Diffuser Lindab |  |  |  |  | DECK | Posisi diffusser | BRANCH SECT. NO. | Grafik Carrier | Pipe Flow Expert |  |  |  | DECK | Posisi diffusser | BRANCH SECT. NO. | Perhitungan Manual | Pipe Flow Expert
|  | 1355 4: Initial; 1355 5: Selected | [13 empty] | DUCT SIZE diameter (in) | DUCT SIZE diameter (in) % | DUCT SIZE diameter (in) % | CFM | CFM Error % | CFM Error % | VELOCITY V (fps) | VELOCITY (fps) Error % | VELOCITY (fps) Error % | DUCT SIZE diameter (mm) | Air Flow (m3/h) |  | Air Flow (m3/h) |  | Curve Loss 1 (m3/h) | Curve Loss 1 (kPa) | Curve Loss 2 (m3/h) | Curve Loss 2 (kPa) | db(A) |  |  |  | DUCT SIZE (in) | DUCT SIZE diameter (in) | DUCT SIZE diameter (in) % | DUCT SIZE diameter (in) % | DUCT SIZE diameter/2 (m) |  |  |  | CFM | CFM | CFM Error % | CFM Error % | VELOCITY V (fps) | VELOCITY (fps) Error % | VELOCITY (fps) Error %
A DECK |  | DUCTING A-AD 01-03 | 736 | 12.731 |  |  | 1.5 | 3 | 1.5 | 6 | 152.4 | 0.0762 | 4000 | 66.6667 | 3.8814 | 12.731 | 3.96 | 1.5152 | 4.9697 |  | 4 | 0.50924 | 0.9144 | 6 | 0 | 0 | 792 | 7.6087 | 7.6087 | 34.795 | -47.8075 | 47.8075 | 152.4 | 1345.6166 | 1345.6166 | 1250.472 | 1250.472 | [5 empty] | A DECK |  | DUCTING A-AD 01-03 | 6 | 6 | 0 | 0 | 0.0762 | A DECK |  | DUCTING A-AD 01-03 | 736 | 736 | 0 | 0 | 34.795 | -47.8075 | 47.8075
A DECK | AB 1 Cabin | A-AD 03-031 | 93 | 3.608 |  |  | 1.5 | 3 | 1.5 | 4 | 101.6 | 0.0508 |  | 0 | 1.1 | 3.608 | 3.96 | 1.0101 | 3.3131 |  |  | 0 | 0.6096 | 2.5 | -37.5 | 37.5 | 82.09 | -11.7312 | 11.7312 | 34.795 | #DIV/0! | #DIV/0! | 63.5 | 139.4718 | 139.4718 | 158.008 | 158.008 | 105 | 0.029 | 158.008 | 0.065 |  | A DECK | AB 1 Cabin | DUCTING A-AD 03-031 | 4 | 2.5 | -37.5 | 37.5 | 0.03175 | A DECK | AB 1 Cabin | DUCTING A-AD 03-031 | 93 | 91.34 | -1.7849 | 1.7849 | 34.795 | #DIV/0! | #DIV/0!
A DECK |  | A-AD 03-04 | 643 | 10.824 |  |  | 1.5 | 3 | 1.5 | 7 | 177.8 | 0.0889 | 2350 | 39.1667 | 3.3 | 10.824 | 3.96 | 1.7677 | 5.798 |  | 1.5 | 0.16236 | 1.0668 | 8 | 14.2857 | 14.2857 | 710 | 10.4199 | 10.4199 | 34.795 | -11.1617 | 11.1617 | 203.2 | 1206.2977 | 1206.2977 | 1092.464 | 1092.464 | [5 empty] | A DECK |  | DUCTING A-AD 03-04 | 7 | 8 | 14.2857 | 14.2857 | 0.1016 | A DECK |  | DUCTING A-AD 03-04 | 643 | 645 | 0.31104 | 0.31104 | 34.795 | -11.1617 | 11.1617
A DECK | Fitter Cabin | A-AD 04-041 | 73 | 14.104 |  |  | 1.5 | 3 | 1.5 | 3 | 76.2 | 0.0381 |  | 0 | 4.3 | 14.104 | 3.96 | 0.75758 | 2.4848 |  |  | 0 | 0.4572 | 3 | 0 | 0 | 74.84 | 2.5205 | 2.5205 | 34.795 | #DIV/0! | #DIV/0! | 76.2 | 127.154 | 127.154 | 124.0278 | 124.0278 | 105 | 0.029 | 124.0278 | 0.04 |  | A DECK | Fitter Cabin | DUCTING A-AD 04-041 | 3 | 2.5 | -16.6667 | 16.6667 | 0.03175 | A DECK | Fitter Cabin | DUCTING A-AD 04-041 | 73 | 76.91 | 5.3562 | 5.3562 | 34.795 | #DIV/0! | #DIV/0!
A DECK |  | A-AD 04-05 | 570 | 5.904 |  |  | 1.5 | 3 | 1.5 | 7 | 177.8 | 0.0889 | 2200 | 36.6667 | 1.8 | 5.904 | 3.96 | 1.7677 | 5.798 |  | 1.3 | 0.076752 | 1.0668 | 8 | 14.2857 | 14.2857 | 635 | 11.4035 | 11.4035 | 34.795 | -5.1045 | 5.1045 | 203.2 | 1078.8719 | 1078.8719 | 968.4362 | 968.4362 | [5 empty] | A DECK |  | DUCTING A-AD 04-05 | 7 | 8 | 14.2857 | 14.2857 | 0.1016 | A DECK |  | DUCTING A-AD 04-05 | 570 | 568 | -0.35088 | 0.35088 | 34.795 | -5.1045 | 5.1045
A DECK | Messman Cabin | A-AD 05-051 | 66 | 9.84 |  |  | 1.5 | 3 | 1.5 | 3 | 76.2 | 0.0381 |  | 0 | 3 | 9.84 | 3.96 | 0.75758 | 2.4848 |  |  | 0 | 0.4572 | 2.5 | -16.6667 | 16.6667 | 64.18 | -2.7576 | 2.7576 | 34.795 | #DIV/0! | #DIV/0! | 63.5 | 109.0425 | 109.0425 | 112.1347 | 112.1347 | 105 | 0.029 | 112.1347 | 0.032 |  | A DECK | Messman Cabin | DUCTING A-AD 05-051 | 3 | 2.5 | -16.6667 | 16.6667 | 0.03175 | A DECK | Messman Cabin | DUCTING A-AD 05-051 | 66 | 63.7 | -3.4848 | 3.4848 | 34.795 | #DIV/0! | #DIV/0!
A DECK |  | A-AD 05-06 | 504 | 8.528 |  |  | 1.5 | 3 | 1.5 | 8 | 203.2 | 0.1016 | 1650 | 27.5 | 2.6 | 8.528 | 3.96 | 2.0202 | 6.6263 |  | 0.55 | 0.046904 | 1.2192 | 8 | 0 | 0 | 571 | 13.2937 | 13.2937 | 34.795 | 26.5273 | 26.5273 | 203.2 | 970.1352 | 970.1352 | 856.3015 | 856.3015 | [5 empty] | A DECK |  | DUCTING A-AD 05-06 | 8 | 8 | 0 | 0 | 0.1016 | A DECK |  | DUCTING A-AD 05-06 | 504 | 504 | 0 | 0 | 34.795 | 26.5273 | 26.5273
A DECK | OS Cabin | A-AD 06-061 | 103 | 9.84 |  |  | 1.5 | 3 | 1.5 | 4 | 101.6 | 0.0508 |  | 0 | 3 | 9.84 | 3.96 | 1.0101 | 3.3131 |  |  | 0 | 0.6096 | 3 | -25 | 25 | 103 | 0 | 0 | 34.795 | #DIV/0! | #DIV/0! | 76.2 | 174.9981 | 174.9981 | 174.9981 | 174.9981 | 105 | 0.029 | 174.9981 | 0.079 | 34 | A DECK | OS Cabin | DUCTING A-AD 06-061 | 4 | 3.5 | -12.5 | 12.5 | 0.04445 | A DECK | OS Cabin | DUCTING A-AD 06-061 | 103 | 103 | 0 | 0 | 34.795 | #DIV/0! | #DIV/0!
A DECK |  | A-AD 06-07 | 401 | 10.168 |  |  | 1.5 | 3 | 1.5 | 8 | 203.2 | 0.1016 | 1400 | 23.3333 | 3.1 | 10.168 | 3.96 | 2.0202 | 6.6263 |  | 0.4 | 0.040672 | 1.2192 | 8 | 0 | 0 | 468 | 16.7082 | 16.7082 | 34.795 | 49.1214 | 49.1214 | 203.2 | 795.1371 | 795.1371 | 681.3033 | 681.3033 | [5 empty] | A DECK |  | DUCTING A-AD 06-07 | 8 | 8 | 0 | 0 | 0.1016 | A DECK |  | DUCTING A-AD 06-07 | 401 | 401 | 0 | 0 | 34.795 | 49.1214 | 49.1214
A DECK | Motorman 1 Cabin | A-AD 07-071 | 102 | 9.84 |  |  | 1.5 | 3 | 1.5 | 4 | 101.6 | 0.0508 |  | 0 | 3 | 9.84 | 3.96 | 1.0101 | 3.3131 |  |  | 0 | 0.6096 | 3 | -25 | 25 | 93.75 | -8.0882 | 8.0882 | 34.795 | #DIV/0! | #DIV/0! | 76.2 | 159.2823 | 159.2823 | 173.2991 | 173.2991 | 105 | 0.029 | 173.2991 | 0.078 | 32 | A DECK | Motorman 1 Cabin | DUCTING A-AD 07-071 | 4 | 3.5 | -12.5 | 12.5 | 0.04445 | A DECK | Motorman 1 Cabin | DUCTING A-AD 07-071 | 102 | 95.78 | -6.098 | 6.098 | 34.795 | #DIV/0! | #DIV/0!
A DECK |  | A-AD 07-08 | 299 | 6.888 |  |  | 1.5 | 3 | 1.5 | 8 | 203.2 | 0.1016 | 1000 | 16.6667 | 2.1 | 6.888 | 3.96 | 2.0202 | 6.6263 |  |  | 0 | 1.2192 | 8 | 0 | 0 | 374 | 25.0836 | 25.0836 | 34.795 | 108.77 | 108.77 | 203.2 | 635.43 | 635.43 | 508.0042 | 508.0042 | [5 empty] | A DECK |  | DUCTING A-AD 07-08 | 8 | 8 | 0 | 0 | 0.1016 | A DECK |  | DUCTING A-AD 07-08 | 299 | 305 | 2.0067 | 2.0067 | 34.795 | 108.77 | 108.77
A DECK | Motorman 2 Cabin | A-AD 08-081 | 109 | 13.448 |  |  | 1.5 | 3 | 1.5 | 4 | 101.6 | 0.0508 |  | 0 | 4.1 | 13.448 | 3.96 | 1.0101 | 3.3131 |  |  | 0 | 0.6096 | 3.5 | -12.5 | 12.5 | 117 | 7.3394 | 7.3394 | 34.795 | #DIV/0! | #DIV/0! | 88.9 | 198.7843 | 198.7843 | 185.1922 | 185.1922 | 105 | 0.029 | 185.1922 | 0.089 | 36 | A DECK | Motorman 2 Cabin | DUCTING A-AD 08-081 | 4 | 4 | 0 | 0 | 0.0508 | A DECK | Motorman 2 Cabin | DUCTING A-AD 08-081 | 109 | 103 | -5.5046 | 5.5046 | 34.795 | #DIV/0! | #DIV/0!
A DECK |  | A-AD 08-09 | 190 | 9.184 |  |  | 1.5 | 3 | 1.5 | 8 | 203.2 | 0.1016 | 1000 | 16.6667 | 2.8 | 9.184 | 3.96 | 2.0202 | 6.6263 |  |  | 0 | 1.2192 | 8 | 0 | 0 | 257 | 35.2632 | 35.2632 | 34.795 | 108.77 | 108.77 | 203.2 | 436.6458 | 436.6458 | 322.8121 | 322.8121 | [5 empty] | A DECK |  | DUCTING A-AD 08-09 | 8 | 8 | 0 | 0 | 0.1016 | A DECK |  | DUCTING A-AD 08-09 | 190 | 202 | 6.3158 | 6.3158 | 34.795 | 108.77 | 108.77
A DECK | AB 2 Cabin | A-AD 09-091 | 72 | 3.936 |  |  | 1.5 | 3 | 1.5 | 3 | 76.2 | 0.0381 |  | 0 | 1.2 | 3.936 | 3.96 | 0.75758 | 2.4848 |  |  | 0 | 0.4572 | 3 | 0 | 0 | 83.62 | 16.1389 | 16.1389 | 34.795 | #DIV/0! | #DIV/0! | 76.2 | 142.0713 | 142.0713 | 122.3288 | 122.3288 | 105 | 0.029 | 122.3288 | 0.039 | 24 | A DECK | AB 2 Cabin | DUCTING A-AD 09-091 | 3 | 2.5 | -16.6667 | 16.6667 | 0.03175 | A DECK | AB 2 Cabin | DUCTING A-AD 09-091 | 72 | 95.15 | 32.1528 | 32.1528 | 34.795 | #DIV/0! | #DIV/0!
A DECK | Hospital | A-AD 09-092 | 118 | 10.496 |  |  | 1.5 | 1.5 | 1.5 | 4 | 101.6 | 0.0508 |  | 0 | 3.2 | 10.496 | 3.96 | 1.0101 | 3.3131 |  |  | 0 | 0.6096 | 4 | 0 | 0 | 173 | 46.6102 | 46.6102 | 34.795 | #DIV/0! | #DIV/0! | 101.6 | 293.9289 | 293.9289 | 200.4833 | 200.4833 | 105 | 0.029 | 200.4833 | 0.104 | 38 | A DECK | Hospital | DUCTING A-AD 09-092 | 4 | 4 | 0 | 0 | 0.0508 | A DECK | Hospital | DUCTING A-AD 09-092 | 118 | 107 | -9.322 | 9.322 | 34.795 | #DIV/0! | #DIV/0!
[29 empty] | 14.3311 | [21 empty] | Rata-rata error laju aliran volumetrik tiap ruangan = | [5 empty] | 7.9629
[27 empty] | 100 | [6 empty] | 169.9011 | 169.9011